## sheet one
HYDRAULIC MODELLING | [12 empty] | ADAM BABULJAK
WATER HAMMER CALCULATIONS
INPUT VALUES
t | 14 | s | time of simulation
Q | 30 | m/s | initial discharge
D | 2.67 | m | pipe diameter
H0 | 725 | m | reservoir level
e | 0.03 | m | pipe wall thickness
E | 196200000000 | N/m2 | pipe elasticity module
K | 1962000000 | N/m2 | water compressibility
θ | 0 | - | pipe inclination
L | 2040 | m | pipe length
4) velocity of water hammer propagation
|  |  | a = | 1018.8696 | m/s | ≈ | 1020 | m/s
5) Maximum pressure in the systém
v0 = | 5.3581 | m/s
ΔHmax = | 556.4914 | m
Hmax = | 1281.4914 | m
Hmin = | 168.5086 | m
WATER HAMMER CALCULATION
lambda | 0.032 | [-] | [5 empty] | D = | 2.67 | m
tclose | 8 | s | [5 empty] | a = | 1020 | m/s
M | 11 | [-] | [5 empty] | H0 = | 725 | m
N | 10 | [-] | [5 empty] | Δx | 204 | m
t | 14 | s | [5 empty] | Δt | 0.1 | s
INITIAL CONTITIONS:
INTERNAL POINTS CALCULATION
velocity [m/s] | A |  |  |  |  | B |  |  |  |  | C |  | head [m] | A |  |  |  |  | B |  |  |  |  | C
Li = | 0 | 204 | 408 | 612 | 816 | 1020 | 1224 | 1428 | 1632 | 1836 | 2040 |  | Li = | 0 | 204 | 408 | 612 | 816 | 1020 | 1224 | 1428 | 1632 | 1836 | 2040
profile i | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  | profile | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
t | [11 empty] | τ | t
0 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 1 | 0 | 723.5367 | 719.9592 | 716.3816 | 712.8041 | 709.2265 | 705.6489 | 702.0714 | 698.4938 | 694.9162 | 691.3387 | 687.7611
0.1 | 5.3581 | 5.3753 | 5.3753 | 5.3753 | 5.3753 | 5.3753 | 5.3753 | 5.3753 | 5.3753 | 5.3753 | 5.1601 | 0.9875 | 0.1 | 723.5367 | 719.9592 | 716.3816 | 712.8041 | 709.2265 | 705.6489 | 702.0714 | 698.4938 | 694.9162 | 691.3387 | 689.5499
0.2 | 5.3666 | 5.3838 | 5.3924 | 5.3924 | 5.3924 | 5.3924 | 5.3924 | 5.3924 | 5.3924 | 5.2769 | 5.1392 | 0.975 | 0.2 | 723.5367 | 719.0648 | 716.3816 | 712.8041 | 709.2265 | 705.6489 | 702.0714 | 698.4938 | 694.9162 | 703.4187 | 701.6299
0.3 | 5.3794 | 5.3966 | 5.4008 | 5.4094 | 5.4094 | 5.4094 | 5.4094 | 5.4094 | 5.2939 | 5.2169 | 5.1024 | 0.9625 | 0.3 | 723.5367 | 718.6205 | 715.4901 | 712.8041 | 709.2265 | 705.6489 | 702.0714 | 698.4938 | 706.9609 | 711.433 | 709.6796
0.4 | 5.3942 | 5.4114 | 5.4134 | 5.4177 | 5.4262 | 5.4262 | 5.4262 | 5.3109 | 5.234 | 5.1689 | 5.0603 | 0.95 | 0.4 | 723.5367 | 718.4012 | 715.0472 | 711.914 | 709.2265 | 705.6489 | 702.0714 | 710.5193 | 714.969 | 718.2766 | 716.5102
0.5 | 5.41 | 5.4272 | 5.4282 | 5.4302 | 5.4345 | 5.443 | 5.3279 | 5.2511 | 5.1861 | 5.1238 | 5.0164 | 0.9375 | 0.5 | 723.5367 | 718.2937 | 714.8301 | 711.4718 | 708.3379 | 705.6489 | 714.0776 | 718.5147 | 721.7847 | 724.7698 | 723.0379
0.6 | 5.4262 | 5.4434 | 5.4438 | 5.4449 | 5.4469 | 5.3362 | 5.268 | 5.2034 | 5.1412 | 5.0796 | 4.9715 | 0.925 | 0.6 | 723.5367 | 718.2396 | 714.7237 | 711.2565 | 707.8964 | 716.7486 | 722.0603 | 725.3005 | 728.2557 | 731.2358 | 729.4896
0.7 | 5.4426 | 5.4597 | 5.4599 | 5.4604 | 5.3467 | 5.2721 | 5.212 | 5.1586 | 5.0971 | 5.0351 | 4.9261 | 0.9125 | 0.7 | 723.5367 | 718.2138 | 714.6701 | 711.151 | 719.6504 | 724.278 | 727.9305 | 731.7488 | 734.7015 | 737.6947 | 735.9825
0.8 | 5.4589 | 5.4761 | 5.4762 | 5.3619 | 5.2859 | 5.2229 | 5.1631 | 5.1061 | 5.0527 | 4.9904 | 4.8801 | 0.9 | 0.8 | 723.5367 | 718.2001 | 714.6446 | 723.046 | 727.5032 | 730.7923 | 733.9161 | 737.2898 | 741.1405 | 744.2315 | 742.5049
0.9 | 5.4752 | 5.4924 | 5.3781 | 5.3018 | 5.2383 | 5.1773 | 5.1172 | 5.0575 | 4.9996 | 4.9451 | 4.8337 | 0.8875 | 0.9 | 723.5367 | 718.1943 | 726.5599 | 730.9654 | 734.1467 | 737.0913 | 740.111 | 743.2697 | 746.7747 | 750.7939 | 749.1014
1 | 5.4915 | 5.3945 | 5.3182 | 5.2548 | 5.1937 | 5.133 | 5.072 | 5.011 | 4.9501 | 4.891 | 4.7867 | 0.875 | 1 | 723.5367 | 730.1 | 734.4861 | 737.6183 | 740.5017 | 743.4237 | 746.4074 | 749.5589 | 752.8789 | 756.5636 | 755.7384
1.1 | 5.3937 | 5.3347 | 5.2715 | 5.2105 | 5.1499 | 5.0887 | 5.0271 | 4.9649 | 4.9026 | 4.8404 | 4.7365 | 0.8625 | 1.1 | 723.5367 | 738.0183 | 741.1189 | 743.97 | 746.8527 | 749.7784 | 752.8335 | 755.98 | 759.3038 | 762.8067 | 761.573
1.2 | 5.2773 | 5.231 | 5.2273 | 5.1668 | 5.1057 | 5.0442 | 4.9818 | 4.919 | 4.8554 | 4.7947 | 4.6862 | 0.85 | 1.2 | 723.5367 | 738.6785 | 747.4527 | 750.3104 | 753.2069 | 756.2235 | 759.3124 | 762.5407 | 765.8639 | 769.0767 | 767.5953
1.3 | 5.1648 | 5.1208 | 5.1268 | 5.1229 | 5.0615 | 4.9992 | 4.9363 | 4.8726 | 4.8113 | 4.7489 | 4.6365 | 0.8375 | 1.3 | 723.5367 | 738.094 | 747.83 | 756.6495 | 759.642 | 762.702 | 765.892 | 769.158 | 772.2693 | 775.5258 | 773.9751
1.4 | 5.0569 | 5.0131 | 5.0169 | 5.0218 | 5.0166 | 4.9539 | 4.8902 | 4.8289 | 4.7663 | 4.7023 | 4.5868 | 0.825 | 1.4 | 723.5367 | 737.6594 | 747.2632 | 757.1317 | 766.1057 | 769.2716 | 772.5088 | 775.5824 | 778.7754 | 782.2099 | 780.5937
1.5 | 4.9519 | 4.9076 | 4.9087 | 4.911 | 4.9145 | 4.9079 | 4.8467 | 4.7841 | 4.7201 | 4.6547 | 4.5369 | 0.8125 | 1.5 | 723.5367 | 737.483 | 746.9446 | 756.7001 | 766.7314 | 775.8734 | 778.9235 | 782.0882 | 785.4782 | 789.016 | 787.4083
1.6 | 4.8481 | 4.8032 | 4.8024 | 4.802 | 4.8028 | 4.8077 | 4.8021 | 4.7382 | 4.6727 | 4.6064 | 4.4867 | 0.8 | 1.6 | 723.5367 | 737.4864 | 746.9136 | 756.5352 | 766.4484 | 776.3538 | 785.4147 | 788.7815 | 792.2839 | 795.9664 | 794.3318
1.7 | 4.7446 | 4.6989 | 4.6972 | 4.6949 | 4.6957 | 4.6974 | 4.6995 | 4.6909 | 4.6247 | 4.5573 | 4.4362 | 0.7875 | 1.7 | 723.5367 | 737.5995 | 747.0712 | 756.6619 | 766.1481 | 775.9705 | 786.1826 | 795.5727 | 799.2243 | 802.9774 | 801.3704
1.8 | 4.6408 | 4.5944 | 4.592 | 4.5915 | 4.5901 | 4.5881 | 4.5867 | 4.5864 | 4.5757 | 4.5078 | 4.385 | 0.775 | 1.8 | 723.5367 | 737.7703 | 747.341 | 756.6848 | 766.184 | 775.9674 | 786.1094 | 796.596 | 806.2206 | 810.097 | 808.4726
1.9 | 4.5363 | 4.4891 | 4.4893 | 4.4878 | 4.4844 | 4.48 | 4.4754 | 4.4719 | 4.4698 | 4.4575 | 4.3335 | 0.7625 | 1.9 | 723.5367 | 737.9744 | 747.3767 | 756.8629 | 766.5045 | 776.3223 | 786.3705 | 796.7371 | 807.4311 | 817.2578 | 815.6656
2 | 4.4311 | 4.386 | 4.3856 | 4.3828 | 4.3782 | 4.3724 | 4.3658 | 4.3593 | 4.3541 | 4.3504 | 4.2813 | 0.75 | 2 | 723.5367 | 737.901 | 747.489 | 757.1955 | 767.0004 | 776.9068 | 786.9479 | 797.1943 | 807.7461 | 818.6334 | 822.91
2.1 | 4.3278 | 4.2815 | 4.2801 | 4.2766 | 4.2713 | 4.2646 | 4.2569 | 4.2485 | 4.2404 | 4.2336 | 4.2137 | 0.7375 | 2.1 | 723.5367 | 737.8807 | 747.7125 | 757.6252 | 767.5958 | 777.6238 | 787.7285 | 797.9538 | 808.3771 | 819.1109 | 824.3633
2.2 | 4.2246 | 4.1766 | 4.1731 | 4.1691 | 4.1635 | 4.1564 | 4.1479 | 4.1385 | 4.1285 | 4.1395 | 4.1383 | 0.725 | 2.2 | 723.5367 | 738.1056 | 748.0097 | 758.111 | 768.2459 | 778.4144 | 788.6265 | 798.9084 | 809.3072 | 817.7592 | 822.7731
2.3 | 4.12 | 4.0706 | 4.0662 | 4.0606 | 4.0547 | 4.0474 | 4.0386 | 4.0285 | 4.0381 | 4.0584 | 4.0609 | 0.7125 | 2.3 | 723.5367 | 738.4488 | 748.4965 | 758.6282 | 768.9264 | 779.2448 | 789.5902 | 799.9758 | 808.2848 | 815.5347 | 820.3282
2.4 | 4.0135 | 3.963 | 3.9587 | 3.9524 | 3.945 | 3.9375 | 3.9285 | 3.9387 | 3.9589 | 3.9817 | 3.9835 | 0.7 | 2.4 | 723.5367 | 738.8098 | 749.0593 | 759.3094 | 769.6238 | 780.0982 | 790.5896 | 798.9644 | 806.202 | 813.1212 | 817.8036
2.5 | 3.9053 | 3.8538 | 3.8497 | 3.8436 | 3.8356 | 3.8266 | 3.838 | 3.8593 | 3.8827 | 3.9059 | 3.9065 | 0.6875 | 2.5 | 723.5367 | 739.1508 | 749.6143 | 760.052 | 770.4777 | 780.9645 | 789.4703 | 796.8173 | 803.8036 | 810.7225 | 815.3713
2.6 | 3.7955 | 3.7431 | 3.7393 | 3.7335 | 3.7257 | 3.7367 | 3.7579 | 3.7825 | 3.8067 | 3.8299 | 3.83 | 0.675 | 2.6 | 723.5367 | 739.4644 | 750.135 | 760.7795 | 771.389 | 779.8481 | 787.1939 | 794.315 | 801.3445 | 808.3497 | 813.0158
2.7 | 3.6842 | 3.631 | 3.6274 | 3.622 | 3.635 | 3.6574 | 3.6816 | 3.7057 | 3.73 | 3.7535 | 3.7536 | 0.6625 | 2.7 | 723.5367 | 739.7549 | 750.6211 | 761.4688 | 770.1485 | 777.6203 | 784.6985 | 791.7307 | 798.8693 | 805.9712 | 810.6802
2.8 | 3.5716 | 3.5176 | 3.5142 | 3.5294 | 3.5541 | 3.5803 | 3.6056 | 3.6294 | 3.6527 | 3.6766 | 3.6774 | 0.65 | 2.8 | 723.5367 | 740.0291 | 751.0805 | 759.9894 | 767.7022 | 775.0046 | 782.1666 | 789.2638 | 796.3659 | 803.5488 | 808.3173
2.9 | 3.4577 | 3.4029 | 3.4201 | 3.4467 | 3.4751 | 3.5026 | 3.5285 | 3.553 | 3.5763 | 3.5996 | 3.6013 | 0.6375 | 2.9 | 723.5367 | 740.2927 | 749.3918 | 757.3169 | 764.8517 | 772.2581 | 779.5808 | 786.8129 | 793.9516 | 801.0584 | 805.8924
3 | 3.3427 | 3.3075 | 3.3359 | 3.3661 | 3.3956 | 3.4236 | 3.4503 | 3.4758 | 3.5001 | 3.5237 | 3.5252 | 0.625 | 3 | 723.5367 | 738.422 | 746.5272 | 754.261 | 761.883 | 769.439 | 776.9154 | 784.2795 | 791.5136 | 798.6249 | 803.3855
3.1 | 3.2469 | 3.2221 | 3.254 | 3.2851 | 3.315 | 3.3436 | 3.3712 | 3.3978 | 3.4234 | 3.4482 | 3.4494 | 0.6125 | 3.1 | 723.5367 | 735.3842 | 743.2932 | 751.1039 | 758.8601 | 766.5519 | 774.1489 | 781.6268 | 788.961 | 796.1455 | 800.927
3.2 | 3.1712 | 3.1491 | 3.1716 | 3.2031 | 3.2335 | 3.2629 | 3.2914 | 3.3191 | 3.3461 | 3.3718 | 3.3738 | 0.6 | 3.2 | 723.5367 | 733.0468 | 739.9665 | 747.9044 | 755.785 | 763.5816 | 771.2745 | 778.8411 | 786.2669 | 793.5925 | 798.4722
3.3 | 3.1084 | 3.0864 | 3.0986 | 3.1204 | 3.1513 | 3.1816 | 3.2111 | 3.2401 | 3.2678 | 3.2945 | 3.2983 | 0.5875 | 3.3 | 723.5367 | 731.7299 | 737.665 | 744.66 | 752.638 | 760.5193 | 768.2853 | 775.9256 | 783.481 | 790.9302 | 795.9263
3.4 | 3.0523 | 3.0298 | 3.0354 | 3.0471 | 3.0688 | 3.0999 | 3.1306 | 3.1601 | 3.1887 | 3.2167 | 3.2226 | 0.575 | 3.4 | 723.5367 | 731.1113 | 736.4296 | 742.41 | 749.4064 | 757.3535 | 765.182 | 772.9364 | 780.5976 | 788.1213 | 793.2337
3.5 | 2.9991 | 2.9763 | 2.9786 | 2.9841 | 2.996 | 3.018 | 3.0492 | 3.0795 | 3.1093 | 3.1388 | 3.1469 | 0.5625 | 3.5 | 723.5367 | 730.8587 | 735.8604 | 741.1853 | 747.1365 | 754.0809 | 762.0162 | 769.8653 | 777.5855 | 785.1545 | 790.3716
3.6 | 2.9471 | 2.9242 | 2.9252 | 2.9277 | 2.9337 | 2.9456 | 2.9673 | 2.9987 | 3.0298 | 3.0607 | 3.071 | 0.55 | 3.6 | 723.5367 | 730.7627 | 735.616 | 740.5936 | 745.8689 | 751.8102 | 758.7759 | 766.6769 | 774.4314 | 782.0261 | 787.3414
3.7 | 2.8958 | 2.8729 | 2.8736 | 2.875 | 2.8776 | 2.8832 | 2.8954 | 2.9179 | 2.9504 | 2.9828 | 2.9951 | 0.5375 | 3.7 | 723.5367 | 730.7152 | 735.4956 | 740.3035 | 745.2739 | 750.573 | 756.4816 | 763.3536 | 771.1268 | 778.7444 | 784.1486
3.8 | 2.8448 | 2.8222 | 2.8229 | 2.8236 | 2.8247 | 2.8276 | 2.834 | 2.8473 | 2.8711 | 2.9049 | 2.9192 | 0.525 | 3.8 | 723.5367 | 730.6696 | 735.4015 | 740.1779 | 745.0114 | 749.9519 | 755.1596 | 760.9423 | 767.6763 | 775.3122 | 780.8033
3.9 | 2.7944 | 2.772 | 2.7724 | 2.7728 | 2.7738 | 2.7758 | 2.7798 | 2.7875 | 2.802 | 2.827 | 2.8434 | 0.5125 | 3.9 | 723.5367 | 730.6096 | 735.3503 | 740.1103 | 744.8578 | 749.6019 | 754.4193 | 759.4914 | 765.1368 | 771.7374 | 777.3101
4 | 2.7445 | 2.7219 | 2.7221 | 2.7228 | 2.7241 | 2.7262 | 2.7295 | 2.7347 | 2.7437 | 2.7594 | 2.7675 | 0.5 | 4 | 723.5367 | 730.5878 | 735.3166 | 740.0307 | 744.7018 | 749.3273 | 753.9378 | 758.6206 | 763.56 | 769.0757 | 773.6748
4.1 | 2.6949 | 2.6722 | 2.6725 | 2.6735 | 2.6753 | 2.6779 | 2.6813 | 2.6858 | 2.6922 | 2.7024 | 2.6936 | 0.4875 | 4.1 | 723.5367 | 730.5922 | 735.2664 | 739.9084 | 744.5008 | 749.039 | 753.5311 | 758.0109 | 762.5651 | 767.3773 | 770.9528
4.2 | 2.6453 | 2.623 | 2.6238 | 2.6252 | 2.6275 | 2.6306 | 2.6344 | 2.639 | 2.6447 | 2.6482 | 2.6222 | 0.475 | 4.2 | 723.5367 | 730.5639 | 735.1822 | 739.7369 | 744.2462 | 748.7056 | 753.1138 | 757.4784 | 761.8315 | 766.69 | 769.6237
4.3 | 2.5962 | 2.5744 | 2.5758 | 2.5779 | 2.5806 | 2.5842 | 2.5884 | 2.5934 | 2.5951 | 2.5918 | 2.553 | 0.4625 | 4.3 | 723.5367 | 730.4775 | 735.0327 | 739.5206 | 743.9424 | 748.322 | 752.6543 | 756.9364 | 761.6043 | 766.8954 | 769.5077
4.4 | 2.5479 | 2.5267 | 2.5287 | 2.5314 | 2.5347 | 2.5386 | 2.5434 | 2.5447 | 2.5407 | 2.5321 | 2.4852 | 0.45 | 4.4 | 723.5367 | 730.3412 | 734.8144 | 739.2389 | 743.5972 | 747.8923 | 752.1461 | 756.7817 | 761.9993 | 767.7438 | 770.2188
4.5 | 2.5007 | 2.4802 | 2.4824 | 2.4856 | 2.4896 | 2.4941 | 2.4951 | 2.4908 | 2.4818 | 2.4696 | 2.418 | 0.4375 | 4.5 | 723.5367 | 730.1739 | 734.5462 | 738.8919 | 743.1898 | 747.4225 | 752.0208 | 757.2096 | 762.9184 | 768.9964 | 771.4205
4.6 | 2.4548 | 2.4349 | 2.4373 | 2.4407 | 2.4451 | 2.4461 | 2.4416 | 2.4323 | 2.4199 | 2.4055 | 2.3512 | 0.425 | 4.6 | 723.5367 | 729.9918 | 734.2503 | 738.498 | 742.7183 | 747.3193 | 752.4865 | 758.157 | 764.2021 | 770.4861 | 772.8914
4.7 | 2.4102 | 2.391 | 2.3934 | 2.3969 | 2.3974 | 2.3928 | 2.3835 | 2.3709 | 2.3561 | 2.3403 | 2.2844 | 0.4125 | 4.7 | 723.5367 | 729.8049 | 733.9427 | 738.0778 | 742.6285 | 747.7827 | 753.4549 | 759.4772 | 765.7188 | 772.1163 | 774.5098
4.8 | 2.367 | 2.3483 | 2.3507 | 2.3502 | 2.3448 | 2.335 | 2.3222 | 2.3075 | 2.2915 | 2.2748 | 2.2176 | 0.4 | 4.8 | 723.5367 | 729.6177 | 733.6317 | 738.0741 | 743.1425 | 748.7635 | 754.7715 | 761.0137 | 767.3846 | 773.8404 | 776.2191
4.9 | 2.3251 | 2.307 | 2.3053 | 2.2987 | 2.2879 | 2.2743 | 2.2591 | 2.243 | 2.2263 | 2.209 | 2.1508 | 0.3875 | 4.9 | 723.5367 | 729.4311 | 733.7482 | 738.6966 | 744.2084 | 750.1294 | 756.3191 | 762.6749 | 769.1281 | 775.641 | 777.9991
5 | 2.2845 | 2.2629 | 2.2551 | 2.2431 | 2.2284 | 2.2122 | 2.1953 | 2.1781 | 2.1607 | 2.143 | 2.0839 | 0.375 | 5 | 723.5367 | 729.6722 | 734.4943 | 739.8814 | 745.6813 | 751.7609 | 758.029 | 764.4292 | 770.924 | 777.4881 | 779.8474
5.1 | 2.2411 | 2.214 | 2.2009 | 2.1849 | 2.1675 | 2.1495 | 2.1313 | 2.1131 | 2.095 | 2.0767 | 2.0169 | 0.3625 | 5.1 | 723.5367 | 730.5422 | 735.8028 | 741.4768 | 747.4307 | 753.577 | 759.8667 | 766.2735 | 772.7818 | 779.3787 | 781.7415
5.2 | 2.1909 | 2.159 | 2.144 | 2.1254 | 2.1062 | 2.0869 | 2.0675 | 2.0484 | 2.0293 | 2.0103 | 1.9497 | 0.35 | 5.2 | 723.5367 | 731.76 | 737.5207 | 743.3486 | 749.3683 | 755.532 | 761.8169 | 768.2146 | 774.7208 | 781.3209 | 783.6695
5.3 | 2.1326 | 2.0974 | 2.0837 | 2.0654 | 2.0449 | 2.0244 | 2.0041 | 1.9838 | 1.9638 | 1.9441 | 1.8825 | 0.3375 | 5.3 | 723.5367 | 732.966 | 739.3007 | 745.4079 | 751.4451 | 757.6034 | 763.8751 | 770.2594 | 776.7463 | 783.3297 | 785.644
5.4 | 2.0669 | 2.0297 | 2.019 | 2.0034 | 1.9838 | 1.9622 | 1.9409 | 1.9197 | 1.8988 | 1.8781 | 1.8151 | 0.325 | 5.4 | 723.5367 | 733.9569 | 740.8475 | 747.3925 | 753.6379 | 759.7832 | 766.0409 | 772.4019 | 778.8609 | 785.4254 | 787.6907
5.5 | 1.9957 | 1.9572 | 1.9495 | 1.9375 | 1.9209 | 1.9004 | 1.878 | 1.856 | 1.8341 | 1.8124 | 1.7477 | 0.3125 | 5.5 | 723.5367 | 734.6861 | 742.043 | 749.0729 | 755.7255 | 762.0703 | 768.305 | 774.6375 | 781.0736 | 787.627 | 789.8354
5.6 | 1.9205 | 1.8813 | 1.8759 | 1.8671 | 1.8542 | 1.8368 | 1.8156 | 1.7926 | 1.7697 | 1.7468 | 1.6802 | 0.3 | 5.6 | 723.5367 | 735.1923 | 742.9062 | 750.3718 | 757.5005 | 764.2422 | 770.6617 | 776.9717 | 783.3962 | 789.9496 | 792.0978
5.7 | 1.8427 | 1.8029 | 1.7991 | 1.7928 | 1.7832 | 1.7696 | 1.7515 | 1.7295 | 1.7054 | 1.6813 | 1.6126 | 0.2875 | 5.7 | 723.5367 | 735.5408 | 743.5166 | 751.3303 | 758.8842 | 766.0871 | 772.9038 | 779.4153 | 785.8403 | 792.4028 | 794.4902
5.8 | 1.7631 | 1.7228 | 1.72 | 1.7153 | 1.7083 | 1.6981 | 1.6836 | 1.6645 | 1.6412 | 1.6158 | 1.5449 | 0.275 | 5.8 | 723.5367 | 735.7916 | 743.9611 | 752.0264 | 759.9135 | 767.5416 | 774.8359 | 781.7674 | 788.4146 | 794.9927 | 797.0194
5.9 | 1.6822 | 1.6415 | 1.6392 | 1.6357 | 1.6303 | 1.6225 | 1.6112 | 1.5955 | 1.5749 | 1.5502 | 1.4772 | 0.2625 | 5.9 | 723.5367 | 735.9892 | 744.2981 | 752.5424 | 760.6812 | 768.6588 | 776.4009 | 783.8304 | 790.9126 | 797.7226 | 799.689
6 | 1.6003 | 1.5592 | 1.5574 | 1.5544 | 1.55 | 1.5436 | 1.5345 | 1.5217 | 1.5045 | 1.4824 | 1.4093 | 0.25 | 6 | 723.5367 | 736.1505 | 744.5675 | 752.9515 | 761.2858 | 769.5378 | 777.6498 | 785.5419 | 793.1315 | 800.3822 | 802.5007
6.1 | 1.5176 | 1.4762 | 1.4746 | 1.4718 | 1.4678 | 1.4621 | 1.4543 | 1.4437 | 1.4294 | 1.4106 | 1.3411 | 0.2375 | 6.1 | 723.5367 | 736.2839 | 744.8012 | 753.31 | 761.8068 | 770.2748 | 778.676 | 786.9474 | 795.0051 | 802.7668 | 805.2439
6.2 | 1.4343 | 1.3925 | 1.3908 | 1.3881 | 1.3841 | 1.3786 | 1.3714 | 1.3621 | 1.3498 | 1.3349 | 1.2724 | 0.225 | 6.2 | 723.5367 | 736.4065 | 745.0239 | 753.6557 | 762.2979 | 770.9434 | 779.5702 | 788.1363 | 796.577 | 804.7125 | 807.6167
6.3 | 1.3503 | 1.308 | 1.3062 | 1.3033 | 1.2991 | 1.2936 | 1.2866 | 1.2777 | 1.2677 | 1.257 | 1.203 | 0.2125 | 6.3 | 723.5367 | 736.5376 | 745.2586 | 754.0111 | 762.7914 | 771.5919 | 780.402 | 789.1975 | 797.8388 | 806.122 | 809.4114
6.4 | 1.2656 | 1.2227 | 1.2206 | 1.2173 | 1.2129 | 1.2071 | 1.2 | 1.1923 | 1.185 | 1.1788 | 1.1331 | 0.2 | 6.4 | 723.5367 | 736.6902 | 745.5226 | 754.3937 | 763.3044 | 772.2489 | 781.2178 | 790.1026 | 798.7385 | 806.984 | 810.5714
6.5 | 1.18 | 1.1364 | 1.134 | 1.1303 | 1.1255 | 1.1194 | 1.113 | 1.1074 | 1.1035 | 1.1014 | 1.0627 | 0.1875 | 6.5 | 723.5367 | 736.8685 | 745.8232 | 754.8152 | 763.8504 | 772.9292 | 781.9483 | 790.7573 | 799.2445 | 807.3547 | 811.1533
6.6 | 1.0933 | 1.049 | 1.0463 | 1.0423 | 1.037 | 1.0315 | 1.0269 | 1.0243 | 1.0238 | 1.0251 | 0.99188 | 0.175 | 6.6 | 723.5367 | 737.0702 | 746.1591 | 755.2793 | 764.4393 | 773.5488 | 782.4677 | 791.0891 | 799.3711 | 807.3229 | 811.2656
6.7 | 1.0054 | 0.96033 | 0.95743 | 0.9531 | 0.94837 | 0.94464 | 0.94292 | 0.94347 | 0.94603 | 0.95005 | 0.92089 | 0.1625 | 6.7 | 723.5367 | 737.2903 | 746.5244 | 755.7826 | 764.977 | 773.977 | 782.6889 | 791.0808 | 799.1658 | 806.9796 | 811.0219
6.8 | 0.91614 | 0.87028 | 0.86724 | 0.86362 | 0.86084 | 0.85993 | 0.86127 | 0.86471 | 0.86977 | 0.87593 | 0.84979 | 0.15 | 6.8 | 723.5367 | 737.5236 | 746.9118 | 756.2215 | 765.3197 | 774.1165 | 782.5897 | 790.7654 | 798.6883 | 806.4007 | 810.5166
6.9 | 0.82547 | 0.7788 | 0.77658 | 0.77507 | 0.77528 | 0.77756 | 0.78181 | 0.78766 | 0.79467 | 0.80246 | 0.77864 | 0.1375 | 6.9 | 723.5367 | 737.7663 | 747.219 | 756.4485 | 765.3606 | 773.9321 | 782.1929 | 790.1973 | 797.9997 | 805.6411 | 809.8174
7 | 0.73332 | 0.68676 | 0.68674 | 0.68833 | 0.69188 | 0.69724 | 0.70403 | 0.71186 | 0.72041 | 0.72946 | 0.70748 | 0.125 | 7 | 723.5367 | 737.9193 | 747.3014 | 756.3578 | 765.0607 | 773.437 | 781.5399 | 789.4276 | 797.1498 | 804.7422 | 808.9675
7.1 | 0.64058 | 0.59545 | 0.59859 | 0.60362 | 0.61037 | 0.61842 | 0.62735 | 0.63685 | 0.6467 | 0.65681 | 0.63635 | 0.1125 | 7.1 | 723.5367 | 737.841 | 747.0568 | 755.9136 | 764.4343 | 772.6689 | 780.6722 | 788.4931 | 796.17 | 803.7309 | 807.9972
7.2 | 0.549 | 0.50625 | 0.51241 | 0.5207 | 0.53022 | 0.54055 | 0.5513 | 0.56226 | 0.5733 | 0.58441 | 0.56527 | 0.1 | 7.2 | 723.5367 | 737.4793 | 746.4523 | 755.1336 | 763.5221 | 771.67 | 779.6226 | 787.4153 | 795.0742 | 802.6217 | 806.9278
7.3 | 0.46041 | 0.42034 | 0.42842 | 0.43907 | 0.45093 | 0.46316 | 0.4755 | 0.48781 | 0.50001 | 0.51209 | 0.49426 | 0.0875 | 7.3 | 723.5367 | 736.8965 | 745.5555 | 754.0613 | 762.3699 | 770.4765 | 778.4139 | 786.2045 | 793.8672 | 801.4186 | 805.7694
7.4 | 0.37601 | 0.33841 | 0.34705 | 0.3587 | 0.37206 | 0.38594 | 0.39972 | 0.4133 | 0.42664 | 0.43975 | 0.42332 | 0.075 | 7.4 | 723.5367 | 736.2092 | 744.5051 | 752.7923 | 761.0163 | 769.1144 | 777.0592 | 784.8665 | 792.5492 | 800.1174 | 804.5212
7.5 | 0.2962 | 0.26062 | 0.26874 | 0.28008 | 0.29375 | 0.30865 | 0.32377 | 0.33859 | 0.35308 | 0.3673 | 0.35247 | 0.0625 | 7.5 | 723.5367 | 735.5266 | 743.4459 | 751.4608 | 759.5375 | 767.5997 | 775.5677 | 783.4046 | 791.1169 | 798.7077 | 803.1734
7.6 | 0.2207 | 0.18668 | 0.19368 | 0.20381 | 0.2167 | 0.23162 | 0.24755 | 0.26358 | 0.27928 | 0.29472 | 0.28172 | 0.05 | 7.6 | 723.5367 | 734.9188 | 742.4822 | 750.1916 | 758.0447 | 765.9915 | 773.9458 | 781.8189 | 789.5634 | 797.1767 | 801.7115
7.7 | 0.14893 | 0.11606 | 0.12178 | 0.13033 | 0.14171 | 0.15563 | 0.17145 | 0.18827 | 0.20525 | 0.22203 | 0.21108 | 0.0375 | 7.7 | 723.5367 | 734.4144 | 741.6645 | 749.0666 | 756.6461 | 764.3913 | 772.2433 | 780.1052 | 787.8789 | 795.5105 | 800.12
7.8 | 0.080177 | 0.048171 | 0.052725 | 0.059688 | 0.069272 | 0.081561 | 0.096368 | 0.11314 | 0.13105 | 0.14928 | 0.14057 | 0.025 | 7.8 | 723.5367 | 734.0123 | 740.9988 | 748.1193 | 755.4136 | 762.8983 | 770.5513 | 778.3038 | 786.0526 | 793.6965 | 798.3847
7.9 | 0.013797 | -0.017523 | -0.01391 | -0.0083217 | -0.00044848 | 0.010021 | 0.023264 | 0.039156 | 0.057178 | 0.076493 | 0.070201 | 0.0125 | 7.9 | 723.5367 | 733.6949 | 740.467 | 747.346 | 754.3717 | 761.5738 | 768.9592 | 776.499 | 784.1217 | 791.7237 | 796.4934
8 | -0.050712 | -0.081471 | -0.078568 | -0.074044 | -0.06757 | -0.058741 | -0.047184 | -0.032694 | -0.01539 | 0.0041936 | 0 | 0 | 8 | 723.5367 | 733.4423 | 740.0421 | 746.7195 | 753.5063 | 760.4327 | 767.5218 | 774.7773 | 782.1703 | 789.6305 | 794.4356
8.1 | -0.11372 | -0.14401 | -0.1416 | -0.13781 | -0.13233 | -0.12477 | -0.1147 | -0.10173 | -0.085676 | -0.066677 | 0 | 0 | 8.1 | 723.5367 | 733.2376 | 739.6948 | 746.2024 | 752.7806 | 759.4543 | 766.2509 | 773.1931 | 780.2862 | 787.5029 | 792.2511
8.2 | -0.17551 | -0.20535 | -0.20324 | -0.19988 | -0.19501 | -0.18828 | -0.17931 | -0.16767 | -0.15301 | -0.10037 | 0 | 0 | 8.2 | 723.5367 | 733.0651 | 739.3979 | 745.7559 | 752.1504 | 758.5988 | 765.1257 | 771.7598 | 778.5257 | 781.8145 | 786.4106
8.3 | -0.23623 | -0.26563 | -0.26362 | -0.26043 | -0.25582 | -0.24953 | -0.24125 | -0.23058 | -0.18236 | -0.11442 | 0 | 0 | 8.3 | 723.5367 | 732.9094 | 739.1262 | 745.346 | 751.5742 | 757.822 | 764.1079 | 770.4584 | 773.2884 | 774.5134 | 778.8944
8.4 | -0.29596 | -0.32485 | -0.32279 | -0.31954 | -0.31494 | -0.30877 | -0.30079 | -0.25593 | -0.19198 | -0.11813 | 0 | 0 | 8.4 | 723.5367 | 732.7556 | 738.8574 | 744.9446 | 751.0177 | 757.0835 | 763.155 | 765.6368 | 766.4467 | 766.6107 | 770.7557
8.5 | -0.35468 | -0.38299 | -0.38075 | -0.37728 | -0.37247 | -0.36617 | -0.32343 | -0.26218 | -0.19169 | -0.1167 | 0 | 0 | 8.5 | 723.5367 | 732.5919 | 738.5739 | 744.5292 | 750.454 | 756.3509 | 758.6129 | 759.144 | 758.9601 | 758.6206 | 762.5419
8.6 | -0.4123 | -0.43995 | -0.43745 | -0.43365 | -0.42849 | -0.38711 | -0.32754 | -0.25919 | -0.1869 | -0.11306 | 0 | 0 | 8.6 | 723.5367 | 732.4106 | 738.2635 | 744.0835 | 749.8627 | 751.984 | 752.3409 | 751.9375 | 751.3193 | 750.7856 | 754.5143
8.7 | -0.46869 | -0.49559 | -0.49282 | -0.48864 | -0.44827 | -0.38985 | -0.32286 | -0.25227 | -0.18056 | -0.1088 | 0 | 0 | 8.7 | 723.5367 | 732.2078 | 737.92 | 743.5972 | 745.6141 | 745.8538 | 745.3102 | 744.5181 | 743.7646 | 743.2005 | 746.7724
8.8 | -0.5237 | -0.54978 | -0.54674 | -0.50741 | -0.44998 | -0.38401 | -0.31457 | -0.24424 | -0.17417 | -0.10473 | 0 | 0 | 8.8 | 723.5367 | 731.983 | 737.5413 | 739.4513 | 739.5896 | 738.9421 | 738.0333 | 737.1394 | 736.4009 | 735.8816 | 739.3301
8.9 | -0.57718 | -0.60239 | -0.56434 | -0.50806 | -0.44314 | -0.3747 | -0.30539 | -0.23648 | -0.16841 | -0.10116 | 0 | 0 | 8.9 | 723.5367 | 731.7369 | 733.5146 | 733.5351 | 732.7815 | 731.7719 | 730.774 | 729.9183 | 729.2581 | 728.8105 | 732.161
9 | -0.62901 | -0.61855 | -0.56368 | -0.50006 | -0.43278 | -0.36453 | -0.29662 | -0.22958 | -0.16348 | -0.098158 | 0 | 0 | 9 | 723.5367 | 727.8582 | 727.7319 | 726.8471 | 725.7205 | 724.6164 | 723.6596 | 722.8948 | 722.3295 | 721.954 | 725.2265
9.1 | -0.64433 | -0.61631 | -0.55425 | -0.48841 | -0.42145 | -0.35471 | -0.28872 | -0.22362 | -0.15933 | -0.095661 | 0 | 0 | 9.1 | 723.5367 | 722.2382 | 721.1929 | 719.9208 | 718.6856 | 717.6114 | 716.7399 | 716.0727 | 715.5922 | 715.2792 | 718.4872
9.2 | -0.62383 | -0.5878 | -0.54103 | -0.47565 | -0.41034 | -0.34565 | -0.28171 | -0.21847 | -0.15581 | -0.093577 | 0 | 0 | 9.2 | 723.5367 | 717.6822 | 714.4303 | 713.0353 | 711.8152 | 710.8121 | 710.027 | 709.4392 | 709.0238 | 708.7567 | 711.91
9.3 | -0.57745 | -0.53844 | -0.50921 | -0.46297 | -0.39986 | -0.33735 | -0.27541 | -0.2139 | -0.15273 | -0.091775 | 0 | 0 | 9.3 | 723.5367 | 714.6786 | 709.5282 | 706.3287 | 705.1653 | 704.2338 | 703.5138 | 702.9799 | 702.605 | 702.3669 | 705.4685
9.4 | -0.51516 | -0.47579 | -0.4604 | -0.43343 | -0.38999 | -0.32962 | -0.26955 | -0.20967 | -0.14987 | -0.090126 | 0 | 0 | 9.4 | 723.5367 | 712.9851 | 706.5804 | 701.6617 | 698.7506 | 697.8697 | 697.1889 | 696.6813 | 696.3243 | 696.0969 | 699.1466
9.5 | -0.44458 | -0.4061 | -0.40003 | -0.38743 | -0.3632 | -0.32219 | -0.26388 | -0.20553 | -0.14707 | -0.088502 | 0 | 0 | 9.5 | 723.5367 | 712.2119 | 705.1213 | 699.0051 | 694.369 | 691.7084 | 691.0394 | 690.5349 | 690.1744 | 689.9438 | 692.9363
9.6 | -0.37077 | -0.33364 | -0.33316 | -0.32982 | -0.31965 | -0.29747 | -0.25817 | -0.20129 | -0.14416 | -0.08681 | 0 | 0 | 9.6 | 723.5367 | 712.0129 | 704.6383 | 697.8305 | 691.965 | 687.541 | 685.0564 | 684.5341 | 684.1555 | 683.9095 | 686.839
9.7 | -0.29672 | -0.26101 | -0.26347 | -0.2654 | -0.26411 | -0.25564 | -0.23488 | -0.19681 | -0.14103 | -0.084976 | 0 | 0 | 9.7 | 723.5367 | 712.1323 | 704.723 | 697.5992 | 691.0038 | 685.3147 | 681.0373 | 678.6785 | 678.2702 | 678.0029 | 680.8612
9.8 | -0.22398 | -0.18957 | -0.19328 | -0.19777 | -0.2014 | -0.20153 | -0.19428 | -0.17463 | -0.13763 | -0.08297 | 0 | 0 | 9.8 | 723.5367 | 712.4013 | 705.0937 | 697.8967 | 690.9496 | 684.5012 | 678.9381 | 674.7748 | 672.5269 | 672.2338 | 675.0143
9.9 | -0.1532 | -0.11991 | -0.1239 | -0.1293 | -0.13521 | -0.14006 | -0.14128 | -0.13511 | -0.11657 | -0.08077 | 0 | 0 | 9.9 | 723.5367 | 712.7193 | 705.5752 | 698.4441 | 691.3944 | 684.5735 | 678.2394 | 672.7874 | 668.7391 | 666.6156 | 669.3106
10 | -0.084524 | -0.052164 | -0.055949 | -0.061351 | -0.067966 | -0.074976 | -0.080893 | -0.083231 | -0.078252 | -0.061028 | 0 | 0 | 10 | 723.5367 | 713.0327 | 706.0698 | 699.0728 | 692.068 | 685.1327 | 678.4231 | 672.2043 | 666.8767 | 662.9648 | 663.7641
10.1 | -0.017829 | 0.013762 | 0.010375 | 0.0053772 | -0.0011252 | -0.00881 | -0.01693 | -0.024044 | -0.027695 | -0.024156 | 0 | 0 | 10.1 | 723.5367 | 713.3177 | 706.5304 | 699.6936 | 692.8111 | 685.9176 | 679.0977 | 672.5126 | 666.4303 | 661.2523 | 660.1917
10.2 | 0.047108 | 0.078053 | 0.075085 | 0.070599 | 0.06453 | 0.056918 | 0.048036 | 0.038603 | 0.030049 | 0.016153 | 0 | 0 | 10.2 | 723.5367 | 713.5673 | 706.9416 | 700.2686 | 693.5432 | 686.776 | 680.0071 | 673.3236 | 666.8882 | 661.8712 | 659.4662
10.3 | 0.11052 | 0.1409 | 0.13827 | 0.13424 | 0.12864 | 0.12137 | 0.11245 | 0.10213 | 0.08245 | 0.050716 | 0 | 0 | 10.3 | 723.5367 | 713.7847 | 707.3055 | 700.7911 | 694.2336 | 687.6326 | 681.002 | 674.3827 | 668.7645 | 664.7394 | 661.5084
10.4 | 0.17259 | 0.20244 | 0.20004 | 0.19631 | 0.19107 | 0.18416 | 0.17546 | 0.15629 | 0.12279 | 0.076117 | 0 | 0 | 10.4 | 723.5367 | 713.9782 | 707.6343 | 701.2704 | 694.8805 | 688.4594 | 682.0082 | 676.4428 | 672.2338 | 669.4229 | 665.7605
10.5 | 0.23346 | 0.26277 | 0.26046 | 0.25686 | 0.25182 | 0.24515 | 0.228 | 0.19611 | 0.14995 | 0.09252 | 0 | 0 | 10.5 | 723.5367 | 714.1588 | 707.9432 | 701.7236 | 695.4962 | 689.256 | 683.9002 | 679.8592 | 677.101 | 675.3808 | 671.5488
10.6 | 0.29318 | 0.32191 | 0.31957 | 0.31596 | 0.31092 | 0.29564 | 0.26579 | 0.22165 | 0.16584 | 0.10167 | 0 | 0 | 10.6 | 723.5367 | 714.3364 | 708.2482 | 702.1689 | 696.0989 | 690.9367 | 687.1066 | 684.5579 | 683.0056 | 682.1206 | 678.2747
10.7 | 0.35173 | 0.37984 | 0.37738 | 0.37361 | 0.35975 | 0.33155 | 0.28928 | 0.23551 | 0.17336 | 0.10566 | 0 | 0 | 10.7 | 723.5367 | 714.5201 | 708.5622 | 702.6234 | 697.6091 | 693.9491 | 691.5938 | 690.2523 | 689.5767 | 689.2618 | 685.4832
10.8 | 0.40906 | 0.43649 | 0.43385 | 0.42116 | 0.39422 | 0.35338 | 0.30125 | 0.24098 | 0.17533 | 0.10636 | 0 | 0 | 10.8 | 723.5367 | 714.7158 | 708.8954 | 704.0022 | 700.4731 | 698.2654 | 697.0937 | 696.6114 | 696.5073 | 696.5426 | 692.8656
10.9 | 0.46509 | 0.49176 | 0.48023 | 0.45443 | 0.41476 | 0.36391 | 0.30508 | 0.24107 | 0.17398 | 0.10517 | 0 | 0 | 10.9 | 723.5367 | 714.9275 | 710.1558 | 706.7446 | 704.6576 | 703.6164 | 703.2815 | 703.3472 | 703.576 | 703.8013 | 700.2333
11 | 0.51968 | 0.53687 | 0.51231 | 0.47382 | 0.42411 | 0.36646 | 0.30373 | 0.23808 | 0.17092 | 0.10306 | 0 | 0 | 11 | 723.5367 | 716.0589 | 712.7765 | 710.8102 | 709.8863 | 709.6718 | 709.8679 | 710.2443 | 710.6397 | 710.9495 | 707.4847
11.1 | 0.56407 | 0.56758 | 0.53043 | 0.48198 | 0.42551 | 0.36393 | 0.29946 | 0.23357 | 0.16715 | 0.10062 | 0 | 0 | 11.1 | 723.5367 | 718.54 | 716.7125 | 715.9165 | 715.8222 | 716.1356 | 716.6324 | 717.1586 | 717.6164 | 717.9477 | 714.5747
11.2 | 0.58966 | 0.57989 | 0.53723 | 0.48211 | 0.42179 | 0.3585 | 0.29378 | 0.22854 | 0.16328 | 0.098196 | 0 | 0 | 11.2 | 723.5367 | 721.8735 | 721.6786 | 721.7222 | 722.1631 | 722.7803 | 723.4239 | 724.0026 | 724.4651 | 724.7856 | 721.4923
11.3 | 0.59257 | 0.57219 | 0.53156 | 0.47704 | 0.41511 | 0.35164 | 0.28759 | 0.22349 | 0.15958 | 0.09593 | 0 | 0 | 11.3 | 723.5367 | 725.3336 | 726.881 | 727.9223 | 728.6773 | 729.4487 | 730.148 | 730.7286 | 731.1704 | 731.4675 | 728.2439
11.4 | 0.57354 | 0.54579 | 0.512 | 0.46456 | 0.4069 | 0.3442 | 0.28136 | 0.21864 | 0.15614 | 0.093857 | 0 | 0 | 11.4 | 723.5367 | 728.3808 | 731.5746 | 733.8328 | 735.2047 | 736.0422 | 736.751 | 737.3139 | 737.7295 | 738.0036 | 734.8429
11.5 | 0.53618 | 0.50394 | 0.4788 | 0.44186 | 0.39366 | 0.33662 | 0.27525 | 0.21401 | 0.15291 | 0.091944 | 0 | 0 | 11.5 | 723.5367 | 730.7547 | 735.3298 | 738.8538 | 741.1946 | 742.5042 | 743.2058 | 743.7502 | 744.1459 | 744.4035 | 741.3026
11.6 | 0.48519 | 0.45063 | 0.43382 | 0.40791 | 0.37159 | 0.32471 | 0.26928 | 0.20953 | 0.14982 | 0.090123 | 0 | 0 | 11.6 | 723.5367 | 732.4162 | 738.0314 | 742.6888 | 746.1505 | 748.3556 | 749.5012 | 750.036 | 750.4229 | 750.6739 | 747.633
11.7 | 0.42508 | 0.38967 | 0.37976 | 0.36357 | 0.33898 | 0.30426 | 0.259 | 0.20509 | 0.14675 | 0.088319 | 0 | 0 | 11.7 | 723.5367 | 733.4546 | 739.7732 | 745.3259 | 749.8474 | 753.1452 | 755.1838 | 756.1723 | 756.5629 | 756.8168 | 753.8388
11.8 | 0.35958 | 0.32424 | 0.31945 | 0.31085 | 0.29624 | 0.27327 | 0.24008 | 0.19621 | 0.14359 | 0.086466 | 0 | 0 | 11.8 | 723.5367 | 734.0109 | 740.7476 | 746.9303 | 752.3188 | 756.6737 | 759.8144 | 761.7092 | 762.565 | 762.8298 | 759.9193
11.9 | 0.29147 | 0.25668 | 0.25536 | 0.25215 | 0.24516 | 0.23207 | 0.2105 | 0.17858 | 0.13594 | 0.084511 | 0 | 0 | 11.9 | 723.5367 | 734.2286 | 741.167 | 747.7395 | 753.7553 | 758.9866 | 763.1976 | 766.2058 | 767.975 | 768.707 | 765.8698
12 | 0.22262 | 0.18859 | 0.1894 | 0.18968 | 0.18799 | 0.18239 | 0.17058 | 0.15022 | 0.11951 | 0.078087 | 0 | 0 | 12 | 723.5367 | 734.2295 | 741.22 | 747.9915 | 754.4067 | 760.2784 | 765.377 | 769.4624 | 772.347 | 773.9895 | 771.6819
12.1 | 0.15416 | 0.12095 | 0.12294 | 0.12526 | 0.12693 | 0.12651 | 0.12212 | 0.11152 | 0.092377 | 0.062947 | 0 | 0 | 12.1 | 723.5367 | 734.1051 | 741.0537 | 747.887 | 754.5142 | 760.7966 | 766.5425 | 771.5174 | 775.4762 | 778.2274 | 776.8953
12.2 | 0.086721 | 0.0543 | 0.056822 | 0.060194 | 0.063797 | 0.066676 | 0.067451 | 0.064283 | 0.05496 | 0.039362 | 0 | 0 | 12.2 | 723.5367 | 733.9184 | 740.7719 | 747.5763 | 754.2767 | 760.7782 | 766.9366 | 772.5558 | 777.3973 | 780.9882 | 780.8338
12.3 | 0.020584 | -0.011112 | -0.0084336 | -0.0046352 | -5.2875e-05 | 0.0047423 | 0.0088403 | 0.010899 | 0.011271 | 0.010953 | 0 | 0 | 12.3 | 723.5367 | 733.7087 | 740.441 | 747.1616 | 753.8403 | 760.4167 | 766.7914 | 772.8164 | 778.0676 | 781.9728 | 782.9573
12.4 | -0.04418 | -0.075214 | -0.072566 | -0.068678 | -0.063688 | -0.057886 | -0.051807 | -0.04417 | -0.033105 | -0.017878 | 0 | 0 | 12.4 | 723.5367 | 733.4974 | 740.0984 | 746.7049 | 753.3017 | 759.8535 | 766.2965 | 772.3031 | 777.3918 | 781.0984 | 783.0345
12.5 | -0.10759 | -0.13801 | -0.13546 | -0.13162 | -0.12651 | -0.12024 | -0.11089 | -0.09581 | -0.073318 | -0.043687 | 0 | 0 | 12.5 | 723.5367 | 733.2934 | 739.7614 | 746.2385 | 752.7181 | 759.1814 | 765.3653 | 770.8719 | 775.334 | 778.4921 | 781.137
12.6 | -0.16971 | -0.19954 | -0.19705 | -0.19328 | -0.18816 | -0.17951 | -0.16423 | -0.14004 | -0.10639 | -0.064564 | 0 | 0 | 12.6 | 723.5367 | 733.0975 | 739.4334 | 745.7746 | 752.1183 | 758.2299 | 763.7568 | 768.3961 | 771.9722 | 774.4238 | 777.5434
12.7 | -0.23058 | -0.25981 | -0.25735 | -0.25358 | -0.24627 | -0.23214 | -0.20865 | -0.17481 | -0.13128 | -0.079982 | 0 | 0 | 12.7 | 723.5367 | 732.9065 | 739.1107 | 745.3132 | 751.2865 | 756.6938 | 761.261 | 764.8574 | 767.4862 | 769.2268 | 772.6271
12.8 | -0.29022 | -0.31882 | -0.31632 | -0.31032 | -0.29756 | -0.27539 | -0.24271 | -0.19988 | -0.14839 | -0.090357 | 0 | 0 | 12.8 | 723.5367 | 732.7153 | 738.7863 | 744.6227 | 749.889 | 754.3178 | 757.7947 | 760.3515 | 762.1124 | 763.2317 | 766.7689
12.9 | -0.3486 | -0.37654 | -0.37177 | -0.36027 | -0.33943 | -0.3081 | -0.26662 | -0.21629 | -0.15895 | -0.096583 | 0 | 0 | 12.9 | 723.5367 | 732.5185 | 738.2272 | 743.3622 | 747.6544 | 750.9904 | 753.409 | 755.0505 | 756.0976 | 756.7259 | 760.3028
13 | -0.40568 | -0.43075 | -0.42047 | -0.40086 | -0.3708 | -0.33064 | -0.28168 | -0.22569 | -0.16448 | -0.099692 | 0 | 0 | 13 | 723.5367 | 732.0866 | 737.0944 | 741.2592 | 744.4643 | 746.7465 | 748.2472 | 749.1562 | 749.6649 | 749.9365 | 753.4932
13.1 | -0.45923 | -0.47817 | -0.45981 | -0.43098 | -0.39205 | -0.34437 | -0.2897 | -0.22986 | -0.16642 | -0.10064 | 0 | 0 | 13.1 | 723.5367 | 731.0843 | 735.1188 | 738.1972 | 740.3523 | 741.7224 | 742.4951 | 742.863 | 742.9962 | 743.0283 | 746.5321
13.2 | -0.50486 | -0.51509 | -0.48866 | -0.45099 | -0.40454 | -0.35111 | -0.29255 | -0.23044 | -0.16603 | -0.10021 | 0 | 0 | 13.2 | 723.5367 | 729.358 | 732.1875 | 734.2131 | 735.4568 | 736.1027 | 736.3399 | 736.3366 | 736.2276 | 736.1122 | 739.5482
13.3 | -0.53781 | -0.53821 | -0.50625 | -0.4622 | -0.41004 | -0.35271 | -0.29185 | -0.22871 | -0.16422 | -0.098974 | 0 | 0 | 13.3 | 723.5367 | 727.0197 | 728.4532 | 729.4489 | 729.9654 | 730.0764 | 729.9462 | 729.7062 | 729.4539 | 729.2565 | 732.6207
13.4 | -0.55459 | -0.54551 | -0.51174 | -0.46529 | -0.41037 | -0.35078 | -0.28888 | -0.22564 | -0.16166 | -0.097333 | 0 | 0 | 13.4 | 723.5367 | 724.3539 | 724.2824 | 724.2078 | 724.0708 | 723.8112 | 723.4448 | 723.0652 | 722.7365 | 722.4996 | 725.7932
13.5 | -0.5538 | -0.53658 | -0.50454 | -0.45991 | -0.40602 | -0.34654 | -0.28457 | -0.22183 | -0.15875 | -0.095523 | 0 | 0 | 13.5 | 723.5367 | 721.6818 | 720.1103 | 718.9069 | 718.0563 | 717.4418 | 716.9325 | 716.4768 | 716.1122 | 715.8603 | 719.0863
13.6 | -0.53609 | -0.51252 | -0.48475 | -0.44528 | -0.39608 | -0.33982 | -0.2795 | -0.21768 | -0.1557 | -0.093667 | 0 | 0 | 13.6 | 723.5367 | 719.2628 | 716.3085 | 713.9615 | 712.2807 | 711.1801 | 710.476 | 709.9813 | 709.602 | 709.3464 | 712.5073
13.7 | -0.50359 | -0.4755 | -0.45327 | -0.42093 | -0.37908 | -0.32904 | -0.27293 | -0.21336 | -0.1526 | -0.091812 | 0 | 0 | 13.7 | 723.5367 | 717.2536 | 713.1163 | 709.6848 | 707.0881 | 705.3174 | 704.2311 | 703.6029 | 703.2167 | 702.9604 | 706.0573
13.8 | -0.45919 | -0.42818 | -0.4117 | -0.38708 | -0.3539 | -0.3122 | -0.26291 | -0.20786 | -0.14948 | -0.089955 | 0 | 0 | 13.8 | 723.5367 | 715.7105 | 710.632 | 706.2451 | 702.724 | 700.1414 | 698.4464 | 697.4682 | 696.9625 | 696.7035 | 699.7358
13.9 | -0.40593 | -0.37327 | -0.36201 | -0.34468 | -0.32022 | -0.28777 | -0.24713 | -0.19903 | -0.14522 | -0.08807 | 0 | 0 | 13.9 | 723.5367 | 714.6155 | 708.8411 | 703.673 | 699.3005 | 695.855 | 693.3803 | 691.8076 | 690.9561 | 690.5779 | 693.5431
14 | -0.34661 | -0.31322 | -0.30628 | -0.29517 | -0.27857 | -0.25516 | -0.2239 | -0.18449 | -0.13762 | -0.085042 | 0 | 0 | 14 | 723.5367 | 713.9057 | 707.6578 | 701.8978 | 696.8056 | 692.5411 | 689.2178 | 686.8697 | 685.4241 | 684.7002 | 687.482

## case a)
HYDRAULIC MODELLING | [22 empty] | ADAM BABULJAK
WATER HAMMER CALCULATIONS
INPUT VALUES
t | 14 | s | time of simulation
Q | 30 | m/s | initial discharge
D | 2.67 | m | pipe diameter
H0 | 725 | m | reservoir level
e | 0.03 | m | pipe wall thickness
E | 196200000000 | N/m2 | pipe elasticity module
K | 1962000000 | N/m2 | water compressibility
θ | 0 | - | pipe inclination
L | 2040 | m | pipe length
4) velocity of water hammer propagation
|  |  | a = | 1018.8696 | m/s | ≈ | 1020 | m/s
5) Maximum pressure in the systém
v0 = | 5.3581 | m/s
ΔHmax = | 556.4914 | m
Hmax = | 1281.4914 | m
Hmin = | 168.5086 | m
WATER HAMMER CALCULATION
lambda | 0 | [-] | [5 empty] | D = | 2.67 | m
tclose | 0 | s | [5 empty] | a = | 1020 | m/s
M | 21 | [-] | [5 empty] | H0 = | 725 | m
N | 20 | [-] | [5 empty] | Δx | 102 | m
t | 14 | s | [5 empty] | Δt | 0.1 | s
INITIAL CONTITIONS:
INTERNAL POINTS CALCULATION
velocity [m/s] | A | [9 empty] | B | [9 empty] | C |  | head [m] | A | [9 empty] | B | [9 empty] | C
Li = | 0 | 102 | 204 | 306 | 408 | 510 | 612 | 714 | 816 | 918 | 1020 | 1122 | 1224 | 1326 | 1428 | 1530 | 1632 | 1734 | 1836 | 1938 | 2040 |  | Li = | 0 | 102 | 204 | 306 | 408 | 510 | 612 | 714 | 816 | 918 | 1020 | 1122 | 1224 | 1326 | 1428 | 1530 | 1632 | 1734 | 1836 | 1938 | 2040
profile i | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 |  | profile | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 11
t | [21 empty] | τ | t
0 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 1 | 0 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367
0.1 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 0 | 0 | 0.1 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367
0.2 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 2.679 | 0 | 0 | 0.2 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 1002.0911 | 1002.0911
0.3 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 2.679 | 1.3395 | 0 | 0 | 0.3 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 1002.0911 | 1141.3683 | 1141.3683
0.4 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 2.679 | 1.3395 | 0.66976 | 0 | 0 | 0.4 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 1002.0911 | 1141.3683 | 1211.0069 | 1211.0069
0.5 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 2.679 | 1.3395 | 0.66976 | 0.33488 | 0 | 0 | 0.5 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 1002.0911 | 1141.3683 | 1211.0069 | 1245.8262 | 1245.8262
0.6 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 2.679 | 1.3395 | 0.66976 | 0.33488 | 0.16744 | 0 | 0 | 0.6 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 1002.0911 | 1141.3683 | 1211.0069 | 1245.8262 | 1263.2359 | 1263.2359
0.7 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 2.679 | 1.3395 | 0.66976 | 0.33488 | 0.16744 | 0.08372 | 0 | 0 | 0.7 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 1002.0911 | 1141.3683 | 1211.0069 | 1245.8262 | 1263.2359 | 1271.9407 | 1271.9407
0.8 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 2.679 | 1.3395 | 0.66976 | 0.33488 | 0.16744 | 0.08372 | 0.04186 | 0 | 0 | 0.8 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 1002.0911 | 1141.3683 | 1211.0069 | 1245.8262 | 1263.2359 | 1271.9407 | 1276.2931 | 1276.2931
0.9 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 2.679 | 1.3395 | 0.66976 | 0.33488 | 0.16744 | 0.08372 | 0.04186 | 0.02093 | 0 | 0 | 0.9 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 1002.0911 | 1141.3683 | 1211.0069 | 1245.8262 | 1263.2359 | 1271.9407 | 1276.2931 | 1278.4693 | 1278.4693
1 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 2.679 | 1.3395 | 0.66976 | 0.33488 | 0.16744 | 0.08372 | 0.04186 | 0.02093 | 0.010465 | 0 | 0 | 1 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 1002.0911 | 1141.3683 | 1211.0069 | 1245.8262 | 1263.2359 | 1271.9407 | 1276.2931 | 1278.4693 | 1279.5574 | 1279.5574
1.1 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 2.679 | 1.3395 | 0.66976 | 0.33488 | 0.16744 | 0.08372 | 0.04186 | 0.02093 | 0.010465 | 0.0052325 | 0 | 0 | 1.1 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 1002.0911 | 1141.3683 | 1211.0069 | 1245.8262 | 1263.2359 | 1271.9407 | 1276.2931 | 1278.4693 | 1279.5574 | 1280.1015 | 1280.1015
1.2 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 2.679 | 1.3395 | 0.66976 | 0.33488 | 0.16744 | 0.08372 | 0.04186 | 0.02093 | 0.010465 | 0.0052325 | 0.0026162 | 0 | 0 | 1.2 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 1002.0911 | 1141.3683 | 1211.0069 | 1245.8262 | 1263.2359 | 1271.9407 | 1276.2931 | 1278.4693 | 1279.5574 | 1280.1015 | 1280.3735 | 1280.3735
1.3 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 2.679 | 1.3395 | 0.66976 | 0.33488 | 0.16744 | 0.08372 | 0.04186 | 0.02093 | 0.010465 | 0.0052325 | 0.0026162 | 0.0013081 | 0 | 0 | 1.3 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 1002.0911 | 1141.3683 | 1211.0069 | 1245.8262 | 1263.2359 | 1271.9407 | 1276.2931 | 1278.4693 | 1279.5574 | 1280.1015 | 1280.3735 | 1280.5095 | 1280.5095
1.4 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 2.679 | 1.3395 | 0.66976 | 0.33488 | 0.16744 | 0.08372 | 0.04186 | 0.02093 | 0.010465 | 0.0052325 | 0.0026162 | 0.0013081 | 0.00065406 | 0 | 0 | 1.4 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 1002.0911 | 1141.3683 | 1211.0069 | 1245.8262 | 1263.2359 | 1271.9407 | 1276.2931 | 1278.4693 | 1279.5574 | 1280.1015 | 1280.3735 | 1280.5095 | 1280.5775 | 1280.5775
1.5 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 2.679 | 1.3395 | 0.66976 | 0.33488 | 0.16744 | 0.08372 | 0.04186 | 0.02093 | 0.010465 | 0.0052325 | 0.0026162 | 0.0013081 | 0.00065406 | 0.00032703 | 0 | 0 | 1.5 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 1002.0911 | 1141.3683 | 1211.0069 | 1245.8262 | 1263.2359 | 1271.9407 | 1276.2931 | 1278.4693 | 1279.5574 | 1280.1015 | 1280.3735 | 1280.5095 | 1280.5775 | 1280.6115 | 1280.6115
1.6 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 2.679 | 1.3395 | 0.66976 | 0.33488 | 0.16744 | 0.08372 | 0.04186 | 0.02093 | 0.010465 | 0.0052325 | 0.0026162 | 0.0013081 | 0.00065406 | 0.00032703 | 0.00016352 | 0 | 0 | 1.6 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 1002.0911 | 1141.3683 | 1211.0069 | 1245.8262 | 1263.2359 | 1271.9407 | 1276.2931 | 1278.4693 | 1279.5574 | 1280.1015 | 1280.3735 | 1280.5095 | 1280.5775 | 1280.6115 | 1280.6285 | 1280.6285
1.7 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 2.679 | 1.3395 | 0.66976 | 0.33488 | 0.16744 | 0.08372 | 0.04186 | 0.02093 | 0.010465 | 0.0052325 | 0.0026162 | 0.0013081 | 0.00065406 | 0.00032703 | 0.00016352 | 8.1758e-05 | 0 | 0 | 1.7 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 1002.0911 | 1141.3683 | 1211.0069 | 1245.8262 | 1263.2359 | 1271.9407 | 1276.2931 | 1278.4693 | 1279.5574 | 1280.1015 | 1280.3735 | 1280.5095 | 1280.5775 | 1280.6115 | 1280.6285 | 1280.637 | 1280.637
1.8 | 5.3581 | 5.3581 | 5.3581 | 2.679 | 1.3395 | 0.66976 | 0.33488 | 0.16744 | 0.08372 | 0.04186 | 0.02093 | 0.010465 | 0.0052325 | 0.0026162 | 0.0013081 | 0.00065406 | 0.00032703 | 0.00016352 | 8.1758e-05 | 4.0879e-05 | 0 | 0 | 1.8 | 723.5367 | 723.5367 | 723.5367 | 1002.0911 | 1141.3683 | 1211.0069 | 1245.8262 | 1263.2359 | 1271.9407 | 1276.2931 | 1278.4693 | 1279.5574 | 1280.1015 | 1280.3735 | 1280.5095 | 1280.5775 | 1280.6115 | 1280.6285 | 1280.637 | 1280.6413 | 1280.6413
1.9 | 5.3581 | 5.3581 | 2.679 | 1.3395 | 0.66976 | 0.33488 | 0.16744 | 0.08372 | 0.04186 | 0.02093 | 0.010465 | 0.0052325 | 0.0026162 | 0.0013081 | 0.00065406 | 0.00032703 | 0.00016352 | 8.1758e-05 | 4.0879e-05 | 2.0439e-05 | 0 | 0 | 1.9 | 723.5367 | 723.5367 | 1002.0911 | 1141.3683 | 1211.0069 | 1245.8262 | 1263.2359 | 1271.9407 | 1276.2931 | 1278.4693 | 1279.5574 | 1280.1015 | 1280.3735 | 1280.5095 | 1280.5775 | 1280.6115 | 1280.6285 | 1280.637 | 1280.6413 | 1280.6434 | 1280.6434
2 | 5.3581 | 2.679 | 1.3395 | 0.66976 | 0.33488 | 0.16744 | 0.08372 | 0.04186 | 0.02093 | 0.010465 | 0.0052325 | 0.0026162 | 0.0013081 | 0.00065406 | 0.00032703 | 0.00016352 | 8.1758e-05 | 4.0879e-05 | 2.0439e-05 | 1.022e-05 | 0 | 0 | 2 | 723.5367 | 1002.0911 | 1141.3683 | 1211.0069 | 1245.8262 | 1263.2359 | 1271.9407 | 1276.2931 | 1278.4693 | 1279.5574 | 1280.1015 | 1280.3735 | 1280.5095 | 1280.5775 | 1280.6115 | 1280.6285 | 1280.637 | 1280.6413 | 1280.6434 | 1280.6445 | 1280.6445
2.1 | 2.679 | 1.3395 | 0.66976 | 0.33488 | 0.16744 | 0.08372 | 0.04186 | 0.02093 | 0.010465 | 0.0052325 | 0.0026162 | 0.0013081 | 0.00065406 | 0.00032703 | 0.00016352 | 8.1758e-05 | 4.0879e-05 | 2.0439e-05 | 1.022e-05 | 5.1099e-06 | 0 | 0 | 2.1 | 723.5367 | 1141.3683 | 1211.0069 | 1245.8262 | 1263.2359 | 1271.9407 | 1276.2931 | 1278.4693 | 1279.5574 | 1280.1015 | 1280.3735 | 1280.5095 | 1280.5775 | 1280.6115 | 1280.6285 | 1280.637 | 1280.6413 | 1280.6434 | 1280.6445 | 1280.645 | 1280.645
2.2 | 8.8818e-16 | -0.66976 | 0.33488 | 0.16744 | 0.08372 | 0.04186 | 0.02093 | 0.010465 | 0.0052325 | 0.0026162 | 0.0013081 | 0.00065406 | 0.00032703 | 0.00016352 | 8.1758e-05 | 4.0879e-05 | 2.0439e-05 | 1.022e-05 | 5.1099e-06 | 2.5549e-06 | 0 | 0 | 2.2 | 723.5367 | 1071.7297 | 1245.8262 | 1263.2359 | 1271.9407 | 1276.2931 | 1278.4693 | 1279.5574 | 1280.1015 | 1280.3735 | 1280.5095 | 1280.5775 | 1280.6115 | 1280.6285 | 1280.637 | 1280.6413 | 1280.6434 | 1280.6445 | 1280.645 | 1280.6453 | 1280.6453
2.3 | -2.0093 | -2.3442 | -1.1721 | 0.08372 | 0.04186 | 0.02093 | 0.010465 | 0.0052325 | 0.0026162 | 0.0013081 | 0.00065406 | 0.00032703 | 0.00016352 | 8.1758e-05 | 4.0879e-05 | 2.0439e-05 | 1.022e-05 | 5.1099e-06 | 2.5549e-06 | 1.2775e-06 | 0 | 0 | 2.3 | 723.5367 | 967.2718 | 1123.9587 | 1271.9407 | 1276.2931 | 1278.4693 | 1279.5574 | 1280.1015 | 1280.3735 | 1280.5095 | 1280.5775 | 1280.6115 | 1280.6285 | 1280.637 | 1280.6413 | 1280.6434 | 1280.6445 | 1280.645 | 1280.6453 | 1280.6454 | 1280.6454
2.4 | -3.3488 | -3.5162 | -2.5953 | -1.2977 | 0.02093 | 0.010465 | 0.0052325 | 0.0026162 | 0.0013081 | 0.00065406 | 0.00032703 | 0.00016352 | 8.1758e-05 | 4.0879e-05 | 2.0439e-05 | 1.022e-05 | 5.1099e-06 | 2.5549e-06 | 1.2775e-06 | 6.3873e-07 | 0 | 0 | 2.4 | 723.5367 | 880.2236 | 993.3863 | 1137.0159 | 1278.4693 | 1279.5574 | 1280.1015 | 1280.3735 | 1280.5095 | 1280.5775 | 1280.6115 | 1280.6285 | 1280.637 | 1280.6413 | 1280.6434 | 1280.6445 | 1280.645 | 1280.6453 | 1280.6454 | 1280.6455 | 1280.6455
2.5 | -4.186 | -4.2697 | -3.6418 | -2.6581 | -1.3291 | 0.0052325 | 0.0026162 | 0.0013081 | 0.00065406 | 0.00032703 | 0.00016352 | 8.1758e-05 | 4.0879e-05 | 2.0439e-05 | 1.022e-05 | 5.1099e-06 | 2.5549e-06 | 1.2775e-06 | 6.3873e-07 | 3.1937e-07 | 0 | 0 | 2.5 | 723.5367 | 819.2898 | 893.2808 | 999.9149 | 1140.2802 | 1280.1015 | 1280.3735 | 1280.5095 | 1280.5775 | 1280.6115 | 1280.6285 | 1280.637 | 1280.6413 | 1280.6434 | 1280.6445 | 1280.645 | 1280.6453 | 1280.6454 | 1280.6455 | 1280.6455 | 1280.6455
2.6 | -4.6883 | -4.7302 | -4.3325 | -3.6732 | -2.6738 | -1.3369 | 0.0013081 | 0.00065406 | 0.00032703 | 0.00016352 | 8.1758e-05 | 4.0879e-05 | 2.0439e-05 | 1.022e-05 | 5.1099e-06 | 2.5549e-06 | 1.2775e-06 | 6.3873e-07 | 3.1937e-07 | 1.5968e-07 | 0 | 0 | 2.6 | 723.5367 | 780.1181 | 825.8184 | 896.5451 | 1001.5471 | 1141.0963 | 1280.5095 | 1280.5775 | 1280.6115 | 1280.6285 | 1280.637 | 1280.6413 | 1280.6434 | 1280.6445 | 1280.645 | 1280.6453 | 1280.6454 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455
2.7 | -4.9813 | -5.0023 | -4.7616 | -4.3482 | -3.6811 | -2.6777 | -1.3389 | 0.00032703 | 0.00016352 | 8.1758e-05 | 4.0879e-05 | 2.0439e-05 | 1.022e-05 | 5.1099e-06 | 2.5549e-06 | 1.2775e-06 | 6.3873e-07 | 3.1937e-07 | 1.5968e-07 | 7.9842e-08 | 0 | 0 | 2.7 | 723.5367 | 756.1798 | 783.3824 | 827.4506 | 897.3612 | 1001.9551 | 1141.3003 | 1280.6115 | 1280.6285 | 1280.637 | 1280.6413 | 1280.6434 | 1280.6445 | 1280.645 | 1280.6453 | 1280.6454 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455
2.8 | -5.1488 | -5.1592 | -5.018 | -4.7694 | -4.3521 | -3.683 | -2.6787 | -1.3394 | 8.1758e-05 | 4.0879e-05 | 2.0439e-05 | 1.022e-05 | 5.1099e-06 | 2.5549e-06 | 1.2775e-06 | 6.3873e-07 | 3.1937e-07 | 1.5968e-07 | 7.9842e-08 | 3.9921e-08 | 0 | 0 | 2.8 | 723.5367 | 742.0345 | 757.812 | 784.1985 | 827.8586 | 897.5652 | 1002.0571 | 1141.3513 | 1280.637 | 1280.6413 | 1280.6434 | 1280.6445 | 1280.645 | 1280.6453 | 1280.6454 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455
2.9 | -5.243 | -5.2482 | -5.1671 | -5.0219 | -4.7714 | -4.3531 | -3.6835 | -2.679 | -1.3395 | 2.0439e-05 | 1.022e-05 | 5.1099e-06 | 2.5549e-06 | 1.2775e-06 | 6.3873e-07 | 3.1937e-07 | 1.5968e-07 | 7.9842e-08 | 3.9921e-08 | 1.996e-08 | 0 | 0 | 2.9 | 723.5367 | 733.8737 | 742.8506 | 758.22 | 784.4025 | 827.9606 | 897.6162 | 1002.0826 | 1141.3641 | 1280.6434 | 1280.6445 | 1280.645 | 1280.6453 | 1280.6454 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455
3 | -5.2953 | -5.2979 | -5.2521 | -5.1691 | -5.0229 | -4.7719 | -4.3534 | -3.6836 | -2.679 | -1.3395 | 5.1099e-06 | 2.5549e-06 | 1.2775e-06 | 6.3873e-07 | 3.1937e-07 | 1.5968e-07 | 7.9842e-08 | 3.9921e-08 | 1.996e-08 | 9.9802e-09 | 0 | 0 | 3 | 723.5367 | 729.2493 | 734.2818 | 743.0546 | 758.322 | 784.4535 | 827.9861 | 897.629 | 1002.089 | 1141.3673 | 1280.645 | 1280.6453 | 1280.6454 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455
3.1 | -5.3241 | -5.3254 | -5.2999 | -5.2531 | -5.1695 | -5.0231 | -4.772 | -4.3534 | -3.6837 | -2.679 | -1.3395 | 1.2775e-06 | 6.3873e-07 | 3.1937e-07 | 1.5968e-07 | 7.9842e-08 | 3.9921e-08 | 1.996e-08 | 9.9802e-09 | 4.9901e-09 | 0 | 0 | 3.1 | 723.5367 | 726.665 | 729.4533 | 734.3838 | 743.1056 | 758.3475 | 784.4663 | 827.9925 | 897.6322 | 1002.0906 | 1141.3681 | 1280.6454 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455
3.2 | -5.3398 | -5.3404 | -5.3264 | -5.3004 | -5.2533 | -5.1697 | -5.0232 | -4.772 | -4.3534 | -3.6837 | -2.679 | -1.3395 | 3.1937e-07 | 1.5968e-07 | 7.9842e-08 | 3.9921e-08 | 1.996e-08 | 9.9802e-09 | 4.9901e-09 | 2.495e-09 | 0 | 0 | 3.2 | 723.5367 | 725.2369 | 726.7671 | 729.5043 | 734.4093 | 743.1184 | 758.3539 | 784.4695 | 827.9941 | 897.633 | 1002.091 | 1141.3683 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455
3.3 | -5.3483 | -5.3486 | -5.3409 | -5.3266 | -5.3005 | -5.2534 | -5.1697 | -5.0232 | -4.772 | -4.3534 | -3.6837 | -2.679 | -1.3395 | 7.9842e-08 | 3.9921e-08 | 1.996e-08 | 9.9802e-09 | 4.9901e-09 | 2.495e-09 | 1.2475e-09 | 0 | 0 | 3.3 | 723.5367 | 724.4548 | 725.2879 | 726.7926 | 729.5171 | 734.4157 | 743.1215 | 758.3555 | 784.4703 | 827.9945 | 897.6332 | 1002.0911 | 1141.3683 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455
3.4 | -5.3528 | -5.353 | -5.3488 | -5.341 | -5.3267 | -5.3005 | -5.2534 | -5.1697 | -5.0232 | -4.772 | -4.3534 | -3.6837 | -2.679 | -1.3395 | 1.996e-08 | 9.9802e-09 | 4.9901e-09 | 2.495e-09 | 1.2475e-09 | 6.2376e-10 | 0 | 0 | 3.4 | 723.5367 | 724.0298 | 724.4803 | 725.3007 | 726.7989 | 729.5203 | 734.4172 | 743.1223 | 758.3559 | 784.4705 | 827.9946 | 897.6332 | 1002.0911 | 1141.3683 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455
3.5 | -5.3553 | -5.3554 | -5.3531 | -5.3489 | -5.3411 | -5.3267 | -5.3005 | -5.2534 | -5.1697 | -5.0232 | -4.772 | -4.3534 | -3.6837 | -2.679 | -1.3395 | 4.9901e-09 | 2.495e-09 | 1.2475e-09 | 6.2376e-10 | 3.1188e-10 | 0 | 0 | 3.5 | 723.5367 | 723.8003 | 724.0425 | 724.4867 | 725.3039 | 726.8005 | 729.5211 | 734.4176 | 743.1225 | 758.356 | 784.4705 | 827.9946 | 897.6332 | 1002.0911 | 1141.3683 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455
3.6 | -5.3566 | -5.3566 | -5.3554 | -5.3532 | -5.3489 | -5.3411 | -5.3267 | -5.3005 | -5.2534 | -5.1697 | -5.0232 | -4.772 | -4.3534 | -3.6837 | -2.679 | -1.3395 | 1.2475e-09 | 6.2376e-10 | 3.1188e-10 | 1.5594e-10 | 0 | 0 | 3.6 | 723.5367 | 723.677 | 723.8067 | 724.0457 | 724.4883 | 725.3047 | 726.8009 | 729.5213 | 734.4177 | 743.1226 | 758.356 | 784.4705 | 827.9946 | 897.6332 | 1002.0911 | 1141.3683 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455
3.7 | -5.3573 | -5.3573 | -5.3567 | -5.3555 | -5.3532 | -5.3489 | -5.3411 | -5.3267 | -5.3005 | -5.2534 | -5.1697 | -5.0232 | -4.772 | -4.3534 | -3.6837 | -2.679 | -1.3395 | 3.1188e-10 | 1.5594e-10 | 7.797e-11 | 0 | 0 | 3.7 | 723.5367 | 723.6111 | 723.6802 | 723.8082 | 724.0465 | 724.4887 | 725.3049 | 726.801 | 729.5213 | 734.4178 | 743.1226 | 758.356 | 784.4705 | 827.9946 | 897.6332 | 1002.0911 | 1141.3683 | 1280.6455 | 1280.6455 | 1280.6455 | 1280.6455
3.8 | -5.3577 | -5.3577 | -5.3573 | -5.3567 | -5.3555 | -5.3532 | -5.3489 | -5.3411 | -5.3267 | -5.3005 | -5.2534 | -5.1697 | -5.0232 | -4.772 | -4.3534 | -3.6837 | -2.679 | -1.3395 | 7.7969e-11 | 3.8984e-11 | 0 | 0 | 3.8 | 723.5367 | 723.5761 | 723.6127 | 723.681 | 723.8086 | 724.0467 | 724.4888 | 725.3049 | 726.8011 | 729.5213 | 734.4178 | 743.1226 | 758.356 | 784.4705 | 827.9946 | 897.6332 | 1002.0911 | 1141.3683 | 1280.6455 | 1280.6455 | 1280.6455
3.9 | -5.3579 | -5.3579 | -5.3577 | -5.3573 | -5.3567 | -5.3555 | -5.3532 | -5.3489 | -5.3411 | -5.3267 | -5.3005 | -5.2534 | -5.1697 | -5.0232 | -4.772 | -4.3534 | -3.6837 | -2.679 | -1.3395 | 1.9493e-11 | 0 | 0 | 3.9 | 723.5367 | 723.5575 | 723.5769 | 723.6131 | 723.6812 | 723.8087 | 724.0468 | 724.4888 | 725.3049 | 726.8011 | 729.5213 | 734.4178 | 743.1226 | 758.356 | 784.4705 | 827.9946 | 897.6332 | 1002.0911 | 1141.3683 | 1280.6455 | 1280.6455
4 | -5.358 | -5.358 | -5.3579 | -5.3577 | -5.3573 | -5.3567 | -5.3555 | -5.3532 | -5.3489 | -5.3411 | -5.3267 | -5.3005 | -5.2534 | -5.1697 | -5.0232 | -4.772 | -4.3534 | -3.6837 | -2.679 | -1.3395 | 0 | 0 | 4 | 723.5367 | 723.5476 | 723.5579 | 723.5771 | 723.6132 | 723.6812 | 723.8088 | 724.0468 | 724.4888 | 725.3049 | 726.8011 | 729.5213 | 734.4178 | 743.1226 | 758.356 | 784.4705 | 827.9946 | 897.6332 | 1002.0911 | 1141.3683 | 1280.6455
4.1 | -5.358 | -5.358 | -5.358 | -5.3579 | -5.3577 | -5.3573 | -5.3567 | -5.3555 | -5.3532 | -5.3489 | -5.3411 | -5.3267 | -5.3005 | -5.2534 | -5.1697 | -5.0232 | -4.772 | -4.3534 | -3.6837 | -2.679 | 0 | 0 | 4.1 | 723.5367 | 723.5425 | 723.5478 | 723.558 | 723.5771 | 723.6132 | 723.6813 | 723.8088 | 724.0468 | 724.4888 | 725.3049 | 726.8011 | 729.5213 | 734.4178 | 743.1226 | 758.356 | 784.4705 | 827.9946 | 897.6332 | 1002.0911 | 1141.3683
4.2 | -5.358 | -5.358 | -5.358 | -5.358 | -5.3579 | -5.3577 | -5.3573 | -5.3567 | -5.3555 | -5.3532 | -5.3489 | -5.3411 | -5.3267 | -5.3005 | -5.2534 | -5.1697 | -5.0232 | -4.772 | -4.3534 | -3.0139 | 0 | 0 | 4.2 | 723.5367 | 723.5397 | 723.5426 | 723.5479 | 723.558 | 723.5771 | 723.6133 | 723.6813 | 723.8088 | 724.0468 | 724.4888 | 725.3049 | 726.8011 | 729.5213 | 734.4178 | 743.1226 | 758.356 | 784.4705 | 827.9946 | 827.9946 | 932.4525
4.3 | -5.3581 | -5.3581 | -5.358 | -5.358 | -5.358 | -5.3579 | -5.3577 | -5.3573 | -5.3567 | -5.3555 | -5.3532 | -5.3489 | -5.3411 | -5.3267 | -5.3005 | -5.2534 | -5.1697 | -5.0232 | -4.1023 | -2.679 | 0 | 0 | 4.3 | 723.5367 | 723.5383 | 723.5398 | 723.5426 | 723.5479 | 723.558 | 723.5771 | 723.6133 | 723.6813 | 723.8088 | 724.0468 | 724.4888 | 725.3049 | 726.8011 | 729.5213 | 734.4178 | 743.1226 | 758.356 | 714.8319 | 653.8982 | 723.5367
4.4 | -5.3581 | -5.3581 | -5.3581 | -5.358 | -5.358 | -5.358 | -5.3579 | -5.3577 | -5.3573 | -5.3567 | -5.3555 | -5.3532 | -5.3489 | -5.3411 | -5.3267 | -5.3005 | -5.2534 | -4.4999 | -3.3488 | -2.093 | 0 | 0 | 4.4 | 723.5367 | 723.5376 | 723.5383 | 723.5398 | 723.5426 | 723.5479 | 723.558 | 723.5771 | 723.6133 | 723.6813 | 723.8088 | 724.0468 | 724.4888 | 725.3049 | 726.8011 | 729.5213 | 734.4178 | 673.484 | 584.2596 | 505.9161 | 549.4403
4.5 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.358 | -5.358 | -5.358 | -5.3579 | -5.3577 | -5.3573 | -5.3567 | -5.3555 | -5.3532 | -5.3489 | -5.3411 | -5.3267 | -4.6308 | -3.579 | -2.4907 | -1.507 | 0 | 0 | 4.5 | 723.5367 | 723.5372 | 723.5376 | 723.5383 | 723.5398 | 723.5426 | 723.5479 | 723.558 | 723.5771 | 723.6133 | 723.6813 | 723.8088 | 724.0468 | 724.4888 | 725.3049 | 726.8011 | 659.8827 | 560.3213 | 464.5682 | 392.7534 | 418.8679
4.6 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.358 | -5.358 | -5.358 | -5.3579 | -5.3577 | -5.3573 | -5.3567 | -5.3555 | -5.3532 | -5.3489 | -4.6713 | -3.6523 | -2.6215 | -1.7372 | -1.0256 | 0 | 0 | 4.6 | 723.5367 | 723.537 | 723.5372 | 723.5376 | 723.5383 | 723.5398 | 723.5426 | 723.5479 | 723.558 | 723.5771 | 723.6133 | 723.6813 | 723.8088 | 724.0468 | 724.4888 | 655.6663 | 552.7046 | 450.9669 | 368.8151 | 312.2338 | 327.4672
4.7 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.358 | -5.358 | -5.358 | -5.3579 | -5.3577 | -5.3573 | -5.3567 | -5.3555 | -4.6834 | -3.6745 | -2.662 | -1.8104 | -1.1564 | -0.66976 | 0 | 0 | 4.7 | 723.5367 | 723.5369 | 723.537 | 723.5372 | 723.5376 | 723.5383 | 723.5398 | 723.5426 | 723.5479 | 723.558 | 723.5771 | 723.6133 | 723.6813 | 723.8088 | 654.4082 | 550.3923 | 446.7505 | 361.1984 | 298.6325 | 257.8286 | 266.5334
4.8 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.358 | -5.358 | -5.358 | -5.3579 | -5.3577 | -5.3573 | -4.6869 | -3.6811 | -2.6741 | -1.8327 | -1.1969 | -0.74301 | -0.42383 | 0 | 0 | 4.8 | 723.5367 | 723.5368 | 723.5369 | 723.537 | 723.5372 | 723.5376 | 723.5383 | 723.5398 | 723.5426 | 723.5479 | 723.558 | 723.5771 | 723.6133 | 654.0427 | 549.7123 | 445.4924 | 358.8862 | 294.4161 | 250.2119 | 222.4653 | 227.3617
4.9 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.358 | -5.358 | -5.358 | -5.3579 | -4.6879 | -3.6829 | -2.6776 | -1.8392 | -1.209 | -0.76525 | -0.46438 | -0.26162 | 0 | 0 | 4.9 | 723.5367 | 723.5368 | 723.5368 | 723.5369 | 723.537 | 723.5372 | 723.5376 | 723.5383 | 723.5398 | 723.5426 | 723.5479 | 723.558 | 653.9385 | 549.5168 | 445.1269 | 358.2061 | 293.158 | 247.8997 | 218.2489 | 200.1592 | 202.8794
5 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.358 | -5.358 | -4.6882 | -3.6835 | -2.6786 | -1.8411 | -1.2125 | -0.77179 | -0.47648 | -0.28386 | -0.15828 | 0 | 0 | 5 | 723.5367 | 723.5368 | 723.5368 | 723.5368 | 723.5369 | 723.537 | 723.5372 | 723.5376 | 723.5383 | 723.5398 | 723.5426 | 653.9093 | 549.4615 | 445.0227 | 358.0106 | 292.7924 | 247.2196 | 216.9907 | 197.8469 | 186.4218 | 187.918
5.1 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -4.6883 | -3.6836 | -2.6789 | -1.8416 | -1.2136 | -0.77367 | -0.48 | -0.2904 | -0.17038 | -0.094185 | 0 | 0 | 5.1 | 723.5367 | 723.5368 | 723.5368 | 723.5368 | 723.5368 | 723.5369 | 723.537 | 723.5372 | 723.5376 | 723.5383 | 653.9012 | 549.4461 | 444.9935 | 357.9554 | 292.6883 | 247.0241 | 216.6252 | 197.1669 | 185.1637 | 178.1251 | 178.9411
5.2 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -4.6883 | -3.6837 | -2.679 | -1.8418 | -1.2138 | -0.7742 | -0.481 | -0.29228 | -0.1739 | -0.10073 | -0.055268 | 0 | 0 | 5.2 | 723.5367 | 723.5368 | 723.5368 | 723.5368 | 723.5368 | 723.5368 | 723.5369 | 723.537 | 723.5372 | 653.899 | 549.4418 | 444.9854 | 357.9399 | 292.6591 | 246.9688 | 216.5211 | 196.9713 | 184.7982 | 177.445 | 173.1946 | 173.6366
5.3 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -4.6883 | -3.6837 | -2.679 | -1.8418 | -1.2139 | -0.77435 | -0.48128 | -0.29282 | -0.1749 | -0.10261 | -0.058784 | -0.032049 | 0 | 0 | 5.3 | 723.5367 | 723.5368 | 723.5368 | 723.5368 | 723.5368 | 723.5368 | 723.5368 | 723.5369 | 653.8984 | 549.4407 | 444.9832 | 357.9357 | 292.651 | 246.9534 | 216.4919 | 196.9161 | 184.6941 | 177.2495 | 172.8291 | 170.3043 | 170.5423
5.4 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -4.6883 | -3.6837 | -2.679 | -1.8418 | -1.2139 | -0.77439 | -0.48136 | -0.29296 | -0.17518 | -0.10314 | -0.059785 | -0.033929 | -0.018395 | 0 | 0 | 5.4 | 723.5367 | 723.5368 | 723.5368 | 723.5368 | 723.5368 | 723.5368 | 723.5368 | 653.8982 | 549.4404 | 444.9826 | 357.9345 | 292.6487 | 246.9492 | 216.4838 | 196.9007 | 184.6648 | 177.1942 | 172.7249 | 170.1088 | 168.6297 | 168.7572
5.5 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -4.6883 | -3.6837 | -2.679 | -1.8418 | -1.2139 | -0.77441 | -0.48138 | -0.293 | -0.17526 | -0.10329 | -0.060066 | -0.034461 | -0.019397 | -0.010465 | 0 | 0 | 5.5 | 723.5367 | 723.5368 | 723.5368 | 723.5368 | 723.5368 | 723.5368 | 653.8982 | 549.4403 | 444.9824 | 357.9342 | 292.6481 | 246.948 | 216.4815 | 196.8964 | 184.6567 | 177.1788 | 172.6957 | 170.0535 | 168.5255 | 167.6691 | 167.7371
5.6 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -4.6883 | -3.6837 | -2.679 | -1.8418 | -1.2139 | -0.77441 | -0.48139 | -0.29302 | -0.17528 | -0.10333 | -0.060144 | -0.034609 | -0.019678 | -0.010996 | -0.005907 | 0 | 0 | 5.6 | 723.5367 | 723.5367 | 723.5368 | 723.5368 | 723.5368 | 653.8982 | 549.4403 | 444.9824 | 357.9341 | 292.648 | 246.9477 | 216.4809 | 196.8953 | 184.6545 | 177.1746 | 172.6876 | 170.0381 | 168.4963 | 167.6138 | 167.1229 | 167.159
5.7 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -4.6883 | -3.6837 | -2.679 | -1.8418 | -1.2139 | -0.77441 | -0.48139 | -0.29302 | -0.17529 | -0.10334 | -0.060166 | -0.03465 | -0.019756 | -0.011145 | -0.006188 | -0.0033112 | 0 | 0 | 5.7 | 723.5367 | 723.5367 | 723.5367 | 723.5368 | 653.8982 | 549.4403 | 444.9824 | 357.9341 | 292.6479 | 246.9476 | 216.4808 | 196.895 | 184.6539 | 177.1734 | 172.6854 | 170.0339 | 168.4882 | 167.5984 | 167.0937 | 166.8147 | 166.8339
5.8 | -5.3581 | -5.3581 | -5.3581 | -4.6883 | -3.6837 | -2.679 | -1.8418 | -1.2139 | -0.77441 | -0.48139 | -0.29302 | -0.17529 | -0.10334 | -0.060172 | -0.034661 | -0.019777 | -0.011185 | -0.006266 | -0.0034594 | -0.0018447 | 0 | 0 | 5.8 | 723.5367 | 723.5367 | 723.5367 | 653.8982 | 549.4403 | 444.9824 | 357.9341 | 292.6479 | 246.9476 | 216.4807 | 196.8949 | 184.6537 | 177.1731 | 172.6848 | 170.0327 | 168.486 | 167.5942 | 167.0856 | 166.7993 | 166.6421 | 166.6522
5.9 | -5.3581 | -5.3581 | -4.6883 | -3.6837 | -2.679 | -1.8418 | -1.2139 | -0.77441 | -0.48139 | -0.29302 | -0.17529 | -0.10334 | -0.060173 | -0.034664 | -0.019783 | -0.011197 | -0.0062874 | -0.0035003 | -0.0019226 | -0.001022 | 0 | 0 | 5.9 | 723.5367 | 723.5367 | 653.8982 | 549.4403 | 444.9824 | 357.9341 | 292.6479 | 246.9476 | 216.4807 | 196.8948 | 184.6537 | 177.173 | 172.6846 | 170.0324 | 168.4854 | 167.593 | 167.0833 | 166.7951 | 166.634 | 166.5459 | 166.5512
6 | -5.3581 | -4.6883 | -3.6837 | -2.679 | -1.8418 | -1.2139 | -0.77441 | -0.48139 | -0.29302 | -0.17529 | -0.10334 | -0.060174 | -0.034665 | -0.019785 | -0.0112 | -0.0062932 | -0.0035114 | -0.001944 | -0.0010629 | -0.00056336 | 0 | 0 | 6 | 723.5367 | 653.8982 | 549.4403 | 444.9824 | 357.9341 | 292.6479 | 246.9476 | 216.4807 | 196.8948 | 184.6537 | 177.173 | 172.6846 | 170.0323 | 168.4852 | 167.5927 | 167.0827 | 166.7939 | 166.6317 | 166.5417 | 166.4926 | 166.4954
6.1 | -4.6883 | -3.6837 | -2.679 | -1.8418 | -1.2139 | -0.77441 | -0.48139 | -0.29302 | -0.17529 | -0.10334 | -0.060174 | -0.034665 | -0.019785 | -0.011201 | -0.0062948 | -0.0035145 | -0.0019498 | -0.001074 | -0.00058476 | -0.00030915 | 0 | 0 | 6.1 | 723.5367 | 549.4403 | 444.9824 | 357.9341 | 292.6479 | 246.9476 | 216.4807 | 196.8948 | 184.6537 | 177.173 | 172.6846 | 170.0323 | 168.4852 | 167.5926 | 167.0826 | 166.7936 | 166.6311 | 166.5405 | 166.4904 | 166.4633 | 166.4647
6.2 | -3.3488 | -2.3442 | -1.8418 | -1.2139 | -0.77441 | -0.48139 | -0.29302 | -0.17529 | -0.10334 | -0.060174 | -0.034665 | -0.019785 | -0.011201 | -0.0062952 | -0.0035153 | -0.0019514 | -0.0010771 | -0.00059059 | -0.00032032 | -0.00016894 | 0 | 0 | 6.2 | 723.5367 | 479.8017 | 357.9341 | 292.6479 | 246.9476 | 216.4807 | 196.8948 | 184.6537 | 177.173 | 172.6845 | 170.0323 | 168.4852 | 167.5926 | 167.0825 | 166.7935 | 166.631 | 166.5402 | 166.4898 | 166.4621 | 166.4472 | 166.4479
6.3 | -1.6744 | -0.8372 | -0.87906 | -0.77441 | -0.48139 | -0.29302 | -0.17529 | -0.10334 | -0.060174 | -0.034665 | -0.019785 | -0.011201 | -0.0062953 | -0.0035155 | -0.0019518 | -0.0010779 | -0.00059216 | -0.00032336 | -0.00017477 | -9.1977e-05 | 0 | 0 | 6.3 | 723.5367 | 462.392 | 327.4672 | 246.9476 | 216.4807 | 196.8948 | 184.6537 | 177.173 | 172.6845 | 170.0323 | 168.4852 | 167.5926 | 167.0825 | 166.7935 | 166.6309 | 166.5401 | 166.4896 | 166.4618 | 166.4466 | 166.4384 | 166.4388
6.4 | 1.4012e-11 | 0.6279 | 0.23023 | -0.14651 | -0.29302 | -0.17529 | -0.10334 | -0.060174 | -0.034665 | -0.019785 | -0.011201 | -0.0062953 | -0.0035156 | -0.0019519 | -0.0010781 | -0.00059259 | -0.00032418 | -0.00017635 | -9.5011e-05 | -4.9901e-05 | 0 | 0 | 6.4 | 723.5367 | 484.1541 | 351.4055 | 251.3 | 196.8948 | 184.6537 | 177.173 | 172.6845 | 170.0323 | 168.4851 | 167.5926 | 167.0825 | 166.7935 | 166.6309 | 166.5401 | 166.4896 | 166.4617 | 166.4464 | 166.4381 | 166.4336 | 166.4338
6.5 | 1.4651 | 1.9046 | 1.3604 | 0.71162 | 0.15959 | -0.10334 | -0.060174 | -0.034665 | -0.019785 | -0.011201 | -0.0062953 | -0.0035156 | -0.001952 | -0.0010782 | -0.0005927 | -0.0003244 | -0.00017677 | -9.583e-05 | -5.1478e-05 | -2.6986e-05 | 0 | 0 | 6.5 | 723.5367 | 525.502 | 407.9868 | 301.3527 | 219.473 | 177.173 | 172.6845 | 170.0323 | 168.4851 | 167.5926 | 167.0825 | 166.7935 | 166.6309 | 166.5401 | 166.4896 | 166.4617 | 166.4464 | 166.438 | 166.4334 | 166.431 | 166.4311
6.6 | 2.6372 | 2.9302 | 2.386 | 1.6665 | 0.9013 | 0.27471 | -0.034665 | -0.019785 | -0.011201 | -0.0062953 | -0.0035156 | -0.001952 | -0.0010782 | -0.00059273 | -0.00032445 | -0.00017689 | -9.6049e-05 | -5.1902e-05 | -2.7805e-05 | -1.4551e-05 | 0 | 0 | 6.6 | 723.5367 | 571.2023 | 475.4492 | 376.1598 | 281.6309 | 207.5038 | 170.0323 | 168.4851 | 167.5926 | 167.0825 | 166.7935 | 166.6309 | 166.5401 | 166.4896 | 166.4617 | 166.4464 | 166.438 | 166.4334 | 166.4309 | 166.4296 | 166.4296
6.7 | 3.5162 | 3.7046 | 3.2363 | 2.5757 | 1.7817 | 0.96997 | 0.31509 | -0.011201 | -0.0062953 | -0.0035156 | -0.001952 | -0.0010782 | -0.00059274 | -0.00032447 | -0.00017692 | -9.6108e-05 | -5.2016e-05 | -2.8024e-05 | -1.4975e-05 | -7.8245e-06 | 0 | 0 | 6.7 | 723.5367 | 612.5502 | 539.3753 | 455.7274 | 364.1907 | 274.4902 | 203.3044 | 167.5926 | 167.0825 | 166.7935 | 166.6309 | 166.5401 | 166.4896 | 166.4617 | 166.4464 | 166.438 | 166.4334 | 166.4309 | 166.4295 | 166.4288 | 166.4289
6.8 | 4.1441 | 4.2619 | 3.8943 | 3.3514 | 2.6444 | 1.8221 | 0.99344 | 0.32858 | -0.0035156 | -0.001952 | -0.0010782 | -0.00059274 | -0.00032447 | -0.00017693 | -9.6124e-05 | -5.2046e-05 | -2.8083e-05 | -1.5089e-05 | -8.044e-06 | -4.1967e-06 | 0 | 0 | 6.8 | 723.5367 | 646.0094 | 592.8284 | 527.4062 | 448.5867 | 359.9913 | 272.0505 | 201.9018 | 166.7935 | 166.6309 | 166.5401 | 166.4896 | 166.4617 | 166.4464 | 166.4379 | 166.4334 | 166.4309 | 166.4295 | 166.4288 | 166.4284 | 166.4284
6.9 | 4.5758 | 4.6478 | 4.377 | 3.963 | 3.3918 | 2.6678 | 1.8355 | 1.0011 | 0.33293 | -0.0010782 | -0.00059274 | -0.00032448 | -0.00017693 | -9.6128e-05 | -5.2054e-05 | -2.8099e-05 | -1.5119e-05 | -8.1027e-06 | -4.3102e-06 | -2.2455e-06 | 0 | 0 | 6.9 | 723.5367 | 671.1718 | 634.0403 | 585.6877 | 523.2068 | 446.147 | 358.5887 | 271.2514 | 201.4502 | 166.5401 | 166.4896 | 166.4617 | 166.4464 | 166.4379 | 166.4334 | 166.4309 | 166.4295 | 166.4288 | 166.4284 | 166.4282 | 166.4282
7 | 4.8636 | 4.9068 | 4.7164 | 4.4174 | 3.9864 | 3.4053 | 2.6755 | 1.8399 | 1.0036 | 0.33429 | -0.00032448 | -0.00017693 | -9.6129e-05 | -5.2056e-05 | -2.8103e-05 | -1.5127e-05 | -8.1183e-06 | -4.3404e-06 | -2.3042e-06 | -1.1989e-06 | 0 | 0 | 7 | 723.5367 | 689.1255 | 664.0311 | 629.8409 | 583.248 | 521.8041 | 445.3479 | 358.1371 | 270.998 | 201.3089 | 166.4617 | 166.4464 | 166.4379 | 166.4334 | 166.4309 | 166.4295 | 166.4288 | 166.4284 | 166.4282 | 166.4281 | 166.4281
7.1 | 5.0507 | 5.0762 | 4.9472 | 4.7399 | 4.4309 | 3.9941 | 3.4096 | 2.678 | 1.8412 | 1.0043 | 0.3347 | -9.6129e-05 | -5.2056e-05 | -2.8104e-05 | -1.5129e-05 | -8.1224e-06 | -4.3485e-06 | -2.3198e-06 | -1.2291e-06 | -6.3873e-07 | 0 | 0 | 7.1 | 723.5367 | 701.4347 | 684.9261 | 661.5914 | 628.4382 | 582.4489 | 521.3525 | 445.0945 | 357.9957 | 270.9196 | 201.2656 | 166.4379 | 166.4334 | 166.4309 | 166.4295 | 166.4288 | 166.4284 | 166.4282 | 166.4281 | 166.428 | 166.428
7.2 | 5.1697 | 5.1846 | 5.0996 | 4.9607 | 4.7476 | 4.4352 | 3.9965 | 3.411 | 2.6787 | 1.8417 | 1.0045 | 0.33483 | -2.8104e-05 | -1.513e-05 | -8.1235e-06 | -4.3506e-06 | -2.3239e-06 | -1.2372e-06 | -6.5433e-07 | -3.3964e-07 | 0 | 0 | 7.2 | 723.5367 | 709.6124 | 698.9949 | 683.5235 | 660.7923 | 627.9866 | 582.1954 | 521.2112 | 445.0161 | 357.9525 | 270.8958 | 201.2527 | 166.4309 | 166.4295 | 166.4288 | 166.4284 | 166.4282 | 166.4281 | 166.428 | 166.428 | 166.428
7.3 | 5.2441 | 5.2527 | 5.1981 | 5.1073 | 4.965 | 4.75 | 4.4366 | 3.9973 | 3.4114 | 2.6789 | 1.8418 | 1.0046 | 0.33486 | -8.1238e-06 | -4.3512e-06 | -2.325e-06 | -1.2393e-06 | -6.5846e-07 | -3.4767e-07 | -1.8027e-07 | 0 | 0 | 7.3 | 723.5367 | 714.9084 | 708.2098 | 698.1958 | 683.0719 | 660.5389 | 627.8453 | 582.1171 | 521.168 | 444.9923 | 357.9395 | 270.8888 | 201.2488 | 166.4288 | 166.4284 | 166.4282 | 166.4281 | 166.428 | 166.428 | 166.428 | 166.428
7.4 | 5.2899 | 5.2948 | 5.2604 | 5.2024 | 5.1098 | 4.9664 | 4.7508 | 4.437 | 3.9975 | 3.4115 | 2.679 | 1.8418 | 1.0046 | 0.33488 | -2.3253e-06 | -1.2398e-06 | -6.5955e-07 | -3.4979e-07 | -1.844e-07 | -9.5514e-08 | 0 | 0 | 7.4 | 723.5367 | 718.2662 | 714.1094 | 707.7582 | 697.9424 | 682.9305 | 660.4605 | 627.8021 | 582.0933 | 521.155 | 444.9853 | 357.9357 | 270.8867 | 201.2477 | 166.4282 | 166.4281 | 166.428 | 166.428 | 166.428 | 166.428 | 166.428
7.5 | 5.3177 | 5.3205 | 5.2991 | 5.2628 | 5.2038 | 5.1105 | 4.9668 | 4.751 | 4.4371 | 3.9976 | 3.4116 | 2.679 | 1.8418 | 1.0046 | 0.33488 | -6.5984e-07 | -3.5035e-07 | -1.8549e-07 | -9.7638e-08 | -5.0525e-08 | 0 | 0 | 7.5 | 723.5367 | 720.3574 | 717.8146 | 713.8559 | 707.6169 | 697.8641 | 682.8873 | 660.4368 | 627.7891 | 582.0863 | 521.1511 | 444.9832 | 357.9346 | 270.8861 | 201.2474 | 166.428 | 166.428 | 166.428 | 166.428 | 166.428 | 166.428
7.6 | 5.3344 | 5.3359 | 5.3229 | 5.3005 | 5.2636 | 5.2042 | 5.1107 | 4.9669 | 4.7511 | 4.4371 | 3.9976 | 3.4116 | 2.679 | 1.8418 | 1.0046 | 0.33488 | -1.8578e-07 | -9.8199e-08 | -5.1616e-08 | -2.6685e-08 | 0 | 0 | 7.6 | 723.5367 | 721.64 | 720.104 | 717.6733 | 713.7776 | 707.5736 | 697.8403 | 682.8743 | 660.4297 | 627.7852 | 582.0842 | 521.15 | 444.9826 | 357.9342 | 270.8859 | 201.2473 | 166.428 | 166.428 | 166.428 | 166.428 | 166.428
7.7 | 5.3443 | 5.3451 | 5.3373 | 5.3237 | 5.3009 | 5.2638 | 5.2043 | 5.1108 | 4.9669 | 4.7511 | 4.4372 | 3.9976 | 3.4116 | 2.679 | 1.8418 | 1.0046 | 0.33488 | -5.1904e-08 | -2.7246e-08 | -1.4074e-08 | 0 | 0 | 7.7 | 723.5367 | 722.4162 | 721.4987 | 720.0257 | 717.6301 | 713.7538 | 707.5606 | 697.8332 | 682.8705 | 660.4276 | 627.7841 | 582.0836 | 521.1497 | 444.9824 | 357.9341 | 270.8859 | 201.2473 | 166.428 | 166.428 | 166.428 | 166.428
7.8 | 5.3501 | 5.3506 | 5.3459 | 5.3377 | 5.3239 | 5.301 | 5.2639 | 5.2044 | 5.1108 | 4.9669 | 4.7511 | 4.4372 | 3.9976 | 3.4116 | 2.679 | 1.8418 | 1.0046 | 0.33488 | -1.4361e-08 | -7.412e-09 | 0 | 0 | 7.8 | 723.5367 | 722.8806 | 722.3379 | 721.4554 | 720.0019 | 717.6171 | 713.7467 | 707.5568 | 697.8312 | 682.8693 | 660.427 | 627.7838 | 582.0834 | 521.1496 | 444.9824 | 357.9341 | 270.8859 | 201.2473 | 166.428 | 166.428 | 166.428
7.9 | 5.3535 | 5.3538 | 5.351 | 5.3461 | 5.3378 | 5.324 | 5.3011 | 5.2639 | 5.2044 | 5.1108 | 4.9669 | 4.7511 | 4.4372 | 3.9976 | 3.4116 | 2.679 | 1.8418 | 1.0046 | 0.33488 | -3.8985e-09 | 0 | 0 | 7.9 | 723.5367 | 723.1555 | 722.8374 | 722.3141 | 721.4425 | 719.9948 | 717.6133 | 713.7447 | 707.5557 | 697.8306 | 682.869 | 660.4268 | 627.7837 | 582.0834 | 521.1496 | 444.9824 | 357.9341 | 270.8859 | 201.2473 | 166.428 | 166.428
8 | 5.3555 | 5.3556 | 5.354 | 5.3511 | 5.3462 | 5.3379 | 5.324 | 5.3011 | 5.2639 | 5.2044 | 5.1108 | 4.9669 | 4.7511 | 4.4372 | 3.9976 | 3.4116 | 2.679 | 1.8418 | 1.0046 | 0.33488 | 0 | 0 | 8 | 723.5367 | 723.3169 | 723.1318 | 722.8244 | 722.3071 | 721.4386 | 719.9928 | 717.6121 | 713.7441 | 707.5554 | 697.8304 | 682.8689 | 660.4268 | 627.7837 | 582.0833 | 521.1496 | 444.9824 | 357.9341 | 270.8859 | 201.2473 | 166.428
8.1 | 5.3566 | 5.3567 | 5.3557 | 5.3541 | 5.3512 | 5.3462 | 5.3379 | 5.324 | 5.3011 | 5.2639 | 5.2044 | 5.1108 | 4.9669 | 4.7511 | 4.4372 | 3.9976 | 3.4116 | 2.679 | 1.8418 | 1.0046 | 0 | 0 | 8.1 | 723.5367 | 723.4107 | 723.3039 | 723.1247 | 722.8205 | 722.305 | 721.4375 | 719.9922 | 717.6118 | 713.7439 | 707.5553 | 697.8303 | 682.8689 | 660.4268 | 627.7837 | 582.0833 | 521.1496 | 444.9824 | 357.9341 | 270.8859 | 201.2473
8.2 | 5.3572 | 5.3573 | 5.3567 | 5.3558 | 5.3541 | 5.3512 | 5.3462 | 5.3379 | 5.324 | 5.3011 | 5.2639 | 5.2044 | 5.1108 | 4.9669 | 4.7511 | 4.4372 | 3.9976 | 3.4116 | 2.679 | 1.6744 | 0 | 0 | 8.2 | 723.5367 | 723.465 | 723.4037 | 723.3 | 723.1226 | 722.8194 | 722.3044 | 721.4372 | 719.992 | 717.6117 | 713.7438 | 707.5552 | 697.8303 | 682.8689 | 660.4268 | 627.7837 | 582.0833 | 521.1496 | 444.9824 | 375.3438 | 288.2955
8.3 | 5.3576 | 5.3576 | 5.3573 | 5.3568 | 5.3558 | 5.3541 | 5.3512 | 5.3462 | 5.3379 | 5.324 | 5.3011 | 5.2639 | 5.2044 | 5.1108 | 4.9669 | 4.7511 | 4.4372 | 3.9976 | 3.2441 | 2.093 | 0 | 0 | 8.3 | 723.5367 | 723.4961 | 723.4611 | 723.4016 | 723.2989 | 723.122 | 722.8191 | 722.3042 | 721.4371 | 719.9919 | 717.6117 | 713.7438 | 707.5552 | 697.8303 | 682.8689 | 660.4268 | 627.7837 | 582.0833 | 538.5592 | 505.9161 | 418.8679
8.4 | 5.3578 | 5.3578 | 5.3576 | 5.3573 | 5.3568 | 5.3558 | 5.3541 | 5.3512 | 5.3462 | 5.3379 | 5.324 | 5.3011 | 5.2639 | 5.2044 | 5.1108 | 4.9669 | 4.7511 | 4.2697 | 3.4116 | 2.1976 | 0 | 0 | 8.4 | 723.5367 | 723.5138 | 723.494 | 723.46 | 723.401 | 723.2986 | 723.1219 | 722.819 | 722.3042 | 721.4371 | 719.9919 | 717.6117 | 713.7438 | 707.5552 | 697.8303 | 682.8689 | 660.4268 | 645.1933 | 643.0171 | 647.3695 | 571.2023
8.5 | 5.3579 | 5.3579 | 5.3578 | 5.3577 | 5.3573 | 5.3568 | 5.3558 | 5.3541 | 5.3512 | 5.3462 | 5.3379 | 5.324 | 5.3011 | 5.2639 | 5.2044 | 5.1108 | 4.7995 | 4.1651 | 3.2232 | 2.0511 | 0 | 0 | 8.5 | 723.5367 | 723.5239 | 723.5127 | 723.4934 | 723.4597 | 723.4008 | 723.2985 | 723.1218 | 722.819 | 722.3041 | 721.4371 | 719.9919 | 717.6117 | 713.7438 | 707.5552 | 697.8303 | 700.2785 | 721.3605 | 754.0036 | 784.4705 | 723.5367
8.6 | 5.358 | 5.358 | 5.3579 | 5.3578 | 5.3577 | 5.3573 | 5.3568 | 5.3558 | 5.3541 | 5.3512 | 5.3462 | 5.3379 | 5.324 | 5.3011 | 5.2639 | 5.0369 | 4.5248 | 3.753 | 2.8046 | 1.7581 | 0 | 0 | 8.6 | 723.5367 | 723.5296 | 723.5233 | 723.5124 | 723.4932 | 723.4596 | 723.4008 | 723.2985 | 723.1218 | 722.819 | 722.3041 | 721.4371 | 719.9919 | 717.6117 | 713.7438 | 724.9649 | 758.7641 | 809.0889 | 862.8139 | 906.3381 | 860.6377
8.7 | 5.358 | 5.358 | 5.358 | 5.3579 | 5.3578 | 5.3577 | 5.3573 | 5.3568 | 5.3558 | 5.3541 | 5.3512 | 5.3462 | 5.3379 | 5.324 | 5.1337 | 4.6779 | 3.9904 | 3.1644 | 2.2879 | 1.4128 | 0 | 0 | 8.7 | 723.5367 | 723.5327 | 723.5292 | 723.5231 | 723.5123 | 723.4932 | 723.4596 | 723.4007 | 723.2985 | 723.1218 | 722.819 | 722.3041 | 721.4371 | 719.9919 | 735.0213 | 774.6776 | 833.7752 | 900.2175 | 961.4233 | 1007.5317 | 974.8886
8.8 | 5.3581 | 5.3581 | 5.358 | 5.358 | 5.3579 | 5.3578 | 5.3577 | 5.3573 | 5.3568 | 5.3558 | 5.3541 | 5.3512 | 5.3462 | 5.1704 | 4.7379 | 4.0872 | 3.3174 | 2.5253 | 1.7725 | 1.0792 | 0 | 0 | 8.8 | 723.5367 | 723.5345 | 723.5326 | 723.5291 | 723.5231 | 723.5123 | 723.4932 | 723.4595 | 723.4007 | 723.2985 | 723.1218 | 722.819 | 722.3041 | 738.8467 | 780.9257 | 843.8316 | 916.131 | 986.1096 | 1044.9352 | 1087.0992 | 1064.6571
8.9 | 5.3581 | 5.3581 | 5.3581 | 5.358 | 5.358 | 5.3579 | 5.3578 | 5.3577 | 5.3573 | 5.3568 | 5.3558 | 5.3541 | 5.1837 | 4.7602 | 4.1239 | 3.3775 | 2.6221 | 1.9256 | 1.3166 | 0.79141 | 0 | 0 | 8.9 | 723.5367 | 723.5355 | 723.5344 | 723.5325 | 723.5291 | 723.523 | 723.5122 | 723.4932 | 723.4595 | 723.4007 | 723.2985 | 723.1218 | 740.2286 | 783.2379 | 847.657 | 922.3791 | 996.1661 | 1060.8487 | 1111.7855 | 1146.9449 | 1131.9835
9 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.358 | 5.358 | 5.3579 | 5.3578 | 5.3577 | 5.3573 | 5.3568 | 5.1883 | 4.768 | 4.1372 | 3.3997 | 2.6588 | 1.9857 | 1.4133 | 0.94447 | 0.56119 | 0 | 0 | 9 | 723.5367 | 723.5361 | 723.5355 | 723.5344 | 723.5325 | 723.5291 | 723.523 | 723.5122 | 723.4932 | 723.4595 | 723.4007 | 740.7081 | 784.0556 | 849.0389 | 924.6913 | 999.9914 | 1067.0968 | 1121.842 | 1162.8584 | 1190.333 | 1180.6081
9.1 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.358 | 5.358 | 5.3579 | 5.3578 | 5.3577 | 5.1899 | 4.7707 | 4.1418 | 3.4076 | 2.6721 | 2.0079 | 1.4501 | 1.0046 | 0.6579 | 0.38688 | 0 | 0 | 9.1 | 723.5367 | 723.5364 | 723.536 | 723.5355 | 723.5344 | 723.5325 | 723.5291 | 723.523 | 723.5122 | 723.4931 | 740.8692 | 784.3345 | 849.5184 | 925.509 | 1001.3734 | 1069.409 | 1125.6674 | 1169.1065 | 1200.3894 | 1220.8339 | 1214.6453
9.2 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.358 | 5.358 | 5.3579 | 5.1904 | 4.7716 | 4.1434 | 3.4103 | 2.6767 | 2.0158 | 1.4634 | 1.0268 | 0.6947 | 0.44697 | 0.2604 | 0 | 0 | 9.2 | 723.5367 | 723.5365 | 723.5364 | 723.536 | 723.5355 | 723.5344 | 723.5325 | 723.5291 | 723.523 | 740.9219 | 784.4269 | 849.6795 | 925.7879 | 1001.8529 | 1070.2267 | 1127.0493 | 1171.4187 | 1204.2148 | 1227.082 | 1241.7204 | 1237.8525
9.3 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.358 | 5.1906 | 4.7719 | 4.1439 | 3.4112 | 2.6783 | 2.0184 | 1.468 | 1.0347 | 0.70799 | 0.46921 | 0.29719 | 0.17169 | 0 | 0 | 9.3 | 723.5367 | 723.5366 | 723.5365 | 723.5364 | 723.536 | 723.5355 | 723.5344 | 723.5325 | 740.9388 | 784.4568 | 849.7322 | 925.8803 | 1002.0139 | 1070.5056 | 1127.5288 | 1172.2364 | 1205.5967 | 1229.3942 | 1245.5457 | 1255.7042 | 1253.324
9.4 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.1906 | 4.772 | 4.1441 | 3.4115 | 2.6788 | 2.0193 | 1.4696 | 1.0373 | 0.7126 | 0.47707 | 0.31048 | 0.19393 | 0.11119 | 0 | 0 | 9.4 | 723.5367 | 723.5367 | 723.5366 | 723.5365 | 723.5364 | 723.536 | 723.5355 | 740.9441 | 784.4663 | 849.7491 | 925.9102 | 1002.0666 | 1070.598 | 1127.6899 | 1172.5153 | 1206.0762 | 1230.2119 | 1246.9276 | 1258.0164 | 1264.8851 | 1263.4399
9.5 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.1906 | 4.772 | 4.1441 | 3.4115 | 2.679 | 2.0196 | 1.4701 | 1.0382 | 0.71415 | 0.47975 | 0.31509 | 0.20179 | 0.12448 | 0.070884 | 0 | 0 | 9.5 | 723.5367 | 723.5367 | 723.5367 | 723.5366 | 723.5365 | 723.5364 | 740.9457 | 784.4692 | 849.7544 | 925.9197 | 1002.0835 | 1070.6279 | 1127.7426 | 1172.6077 | 1206.2373 | 1230.4908 | 1247.4071 | 1258.8341 | 1266.267 | 1270.8101 | 1269.943
9.6 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.1906 | 4.772 | 4.1441 | 3.4116 | 2.679 | 2.0197 | 1.4703 | 1.0385 | 0.71465 | 0.48064 | 0.31664 | 0.20448 | 0.12909 | 0.078748 | 0.044563 | 0 | 0 | 9.6 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 723.5366 | 740.9462 | 784.4701 | 849.756 | 925.9226 | 1002.0888 | 1070.6374 | 1127.7594 | 1172.6376 | 1206.29 | 1230.5832 | 1247.5682 | 1259.113 | 1266.7465 | 1271.6278 | 1274.5765 | 1274.0617
9.7 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.1906 | 4.772 | 4.1441 | 3.4116 | 2.679 | 2.0197 | 1.4703 | 1.0386 | 0.71482 | 0.48093 | 0.31715 | 0.20536 | 0.13064 | 0.081431 | 0.049175 | 0.02767 | 0 | 0 | 9.7 | 723.5367 | 723.5367 | 723.5367 | 723.5367 | 740.9463 | 784.4704 | 849.7565 | 925.9235 | 1002.0904 | 1070.6403 | 1127.7647 | 1172.6471 | 1206.3069 | 1230.6131 | 1247.6209 | 1259.2054 | 1266.9075 | 1271.9067 | 1275.056 | 1276.9387 | 1276.6358
9.8 | 5.3581 | 5.3581 | 5.3581 | 5.1906 | 4.772 | 4.1441 | 3.4116 | 2.679 | 2.0197 | 1.4703 | 1.0386 | 0.71487 | 0.48102 | 0.31731 | 0.20565 | 0.13115 | 0.08232 | 0.050724 | 0.030353 | 0.01699 | 0 | 0 | 9.8 | 723.5367 | 723.5367 | 723.5367 | 740.9464 | 784.4705 | 849.7566 | 925.9238 | 1002.0909 | 1070.6413 | 1127.7663 | 1172.65 | 1206.3122 | 1230.6226 | 1247.6378 | 1259.2353 | 1266.9602 | 1271.9991 | 1275.2171 | 1277.2176 | 1278.4024 | 1278.2257
9.9 | 5.3581 | 5.3581 | 5.1906 | 4.772 | 4.1441 | 3.4116 | 2.679 | 2.0197 | 1.4703 | 1.0386 | 0.71488 | 0.48105 | 0.31736 | 0.20574 | 0.13131 | 0.082607 | 0.051231 | 0.031241 | 0.01854 | 0.010328 | 0 | 0 | 9.9 | 723.5367 | 723.5367 | 740.9464 | 784.4705 | 849.7567 | 925.9239 | 1002.0911 | 1070.6415 | 1127.7668 | 1172.6509 | 1206.3138 | 1230.6255 | 1247.6431 | 1259.2448 | 1266.9771 | 1272.029 | 1275.2698 | 1277.31 | 1278.5635 | 1279.2996 | 1279.1974
10 | 5.3581 | 5.1906 | 4.772 | 4.1441 | 3.4116 | 2.679 | 2.0197 | 1.4703 | 1.0386 | 0.71489 | 0.48106 | 0.31738 | 0.20577 | 0.13136 | 0.082698 | 0.051393 | 0.031529 | 0.019046 | 0.011217 | 0.0062216 | 0 | 0 | 10 | 723.5367 | 740.9464 | 784.4705 | 849.7567 | 925.9239 | 1002.0911 | 1070.6416 | 1127.767 | 1172.6512 | 1206.3143 | 1230.6264 | 1247.6447 | 1259.2477 | 1266.9824 | 1272.0385 | 1275.2866 | 1277.3399 | 1278.6162 | 1279.392 | 1279.8442 | 1279.7854
10.1 | 5.1906 | 4.772 | 4.1441 | 3.4116 | 2.679 | 2.0197 | 1.4703 | 1.0387 | 0.71489 | 0.48106 | 0.31738 | 0.20578 | 0.13138 | 0.082726 | 0.051444 | 0.03162 | 0.019209 | 0.011505 | 0.0067284 | 0.0037168 | 0 | 0 | 10.1 | 723.5367 | 784.4705 | 849.7567 | 925.9239 | 1002.0911 | 1070.6416 | 1127.767 | 1172.6513 | 1206.3144 | 1230.6267 | 1247.6452 | 1259.2486 | 1266.984 | 1272.0414 | 1275.2919 | 1277.3494 | 1278.633 | 1279.4219 | 1279.8969 | 1280.1719 | 1280.1383
10.2 | 4.6883 | 4.0604 | 3.4116 | 2.679 | 2.0197 | 1.4703 | 1.0387 | 0.71489 | 0.48106 | 0.31738 | 0.20578 | 0.13138 | 0.082735 | 0.05146 | 0.031648 | 0.019259 | 0.011596 | 0.0068906 | 0.0040042 | 0.0022036 | 0 | 0 | 10.2 | 723.5367 | 841.0519 | 925.9239 | 1002.0911 | 1070.6416 | 1127.7671 | 1172.6513 | 1206.3145 | 1230.6268 | 1247.6454 | 1259.2489 | 1266.9845 | 1272.0423 | 1275.2936 | 1277.3523 | 1278.6383 | 1279.4314 | 1279.9138 | 1280.2018 | 1280.3674 | 1280.3483
10.3 | 3.8093 | 3.0767 | 2.5953 | 2.0197 | 1.4703 | 1.0387 | 0.71489 | 0.48106 | 0.31738 | 0.20578 | 0.13138 | 0.082738 | 0.051464 | 0.031657 | 0.019275 | 0.011624 | 0.0069415 | 0.0040953 | 0.0023658 | 0.0012974 | 0 | 0 | 10.3 | 723.5367 | 891.1046 | 993.3863 | 1070.6416 | 1127.7671 | 1172.6513 | 1206.3145 | 1230.6268 | 1247.6454 | 1259.249 | 1266.9847 | 1272.0426 | 1275.2941 | 1277.3532 | 1278.64 | 1279.4343 | 1279.9191 | 1280.2112 | 1280.3843 | 1280.4832 | 1280.4724
10.4 | 2.6372 | 1.9046 | 1.6849 | 1.3866 | 1.0387 | 0.71489 | 0.48106 | 0.31738 | 0.20578 | 0.13138 | 0.082739 | 0.051466 | 0.03166 | 0.01928 | 0.011633 | 0.0069573 | 0.0041237 | 0.0024167 | 0.0013885 | 0.00075899 | 0 | 0 | 10.4 | 723.5367 | 921.5715 | 1035.8223 | 1119.0622 | 1172.6513 | 1206.3145 | 1230.6268 | 1247.6454 | 1259.249 | 1266.9847 | 1272.0427 | 1275.2942 | 1277.3535 | 1278.6405 | 1279.4353 | 1279.9207 | 1280.2142 | 1280.3896 | 1280.4927 | 1280.5513 | 1280.5453
10.5 | 1.3186 | 0.65929 | 0.69592 | 0.70377 | 0.63117 | 0.48106 | 0.31738 | 0.20578 | 0.13138 | 0.082739 | 0.051466 | 0.03166 | 0.019281 | 0.011635 | 0.006962 | 0.0041324 | 0.0024325 | 0.0014169 | 0.00080992 | 0.00044138 | 0 | 0 | 10.5 | 723.5367 | 929.1882 | 1047.2474 | 1137.832 | 1197.6097 | 1230.6268 | 1247.6454 | 1259.249 | 1266.9847 | 1272.0427 | 1275.2943 | 1277.3536 | 1278.6406 | 1279.4355 | 1279.9212 | 1280.2151 | 1280.3912 | 1280.4956 | 1280.5566 | 1280.5912 | 1280.5878
10.6 | -3.7405e-10 | -0.54941 | -0.3218 | -0.05952 | 0.14618 | 0.23366 | 0.20578 | 0.13138 | 0.082739 | 0.051466 | 0.031661 | 0.019282 | 0.011636 | 0.0069635 | 0.004135 | 0.0024373 | 0.0014256 | 0.00082566 | 0.00046975 | 0.00025527 | 0 | 0 | 10.6 | 723.5367 | 917.7632 | 1031.1979 | 1125.7949 | 1195.8075 | 1238.9406 | 1259.249 | 1266.9847 | 1272.0427 | 1275.2943 | 1277.3536 | 1278.6407 | 1279.4356 | 1279.9214 | 1280.2154 | 1280.3917 | 1280.4965 | 1280.5583 | 1280.5941 | 1280.6143 | 1280.6124
10.7 | -1.2087 | -1.6404 | -1.3049 | -0.87939 | -0.45703 | -0.1291 | 0.047665 | 0.082739 | 0.051466 | 0.031661 | 0.019282 | 0.011636 | 0.0069639 | 0.0041358 | 0.0024387 | 0.0014282 | 0.00083046 | 0.00047845 | 0.00027101 | 0.00014688 | 0 | 0 | 10.7 | 723.5367 | 894.0969 | 996.3106 | 1089.1734 | 1167.1258 | 1224.4297 | 1258.2799 | 1272.0427 | 1275.2943 | 1277.3536 | 1278.6407 | 1279.4356 | 1279.9214 | 1280.2155 | 1280.3919 | 1280.4968 | 1280.5588 | 1280.595 | 1280.6159 | 1280.6277 | 1280.6266
10.8 | -2.2447 | -2.5685 | -2.198 | -1.7024 | -1.1547 | -0.64302 | -0.25214 | -0.032253 | 0.031661 | 0.019282 | 0.011636 | 0.006964 | 0.004136 | 0.0024391 | 0.001429 | 0.0008319 | 0.00048108 | 0.00027581 | 0.00015558 | 8.4114e-05 | 0 | 0 | 10.8 | 723.5367 | 864.9221 | 952.0724 | 1037.6415 | 1117.7956 | 1186.4651 | 1237.2234 | 1266.5895 | 1277.3536 | 1278.6407 | 1279.4356 | 1279.9214 | 1280.2155 | 1280.3919 | 1280.4969 | 1280.5589 | 1280.5953 | 1280.6164 | 1280.6286 | 1280.6354 | 1280.6348
10.9 | -3.0865 | -3.3203 | -2.966 | -2.4733 | -1.8884 | -1.2777 | -0.72294 | -0.30322 | -0.064438 | 0.011636 | 0.0069641 | 0.0041361 | 0.0024393 | 0.0014292 | 0.00083233 | 0.00048187 | 0.00027725 | 0.00015822 | 8.891e-05 | 4.7955e-05 | 0 | 0 | 10.9 | 723.5367 | 835.3733 | 906.2531 | 980.6946 | 1056.9808 | 1130.5893 | 1194.7747 | 1242.5343 | 1269.9359 | 1279.4356 | 1279.9214 | 1280.2155 | 1280.3919 | 1280.4969 | 1280.559 | 1280.5954 | 1280.6166 | 1280.6289 | 1280.6359 | 1280.6398 | 1280.6395
11 | -3.7412 | -3.9049 | -3.5956 | -3.152 | -2.5963 | -1.9683 | -1.3288 | -0.75513 | -0.32324 | -0.076756 | 0.0041361 | 0.0024393 | 0.0014293 | 0.00083246 | 0.00048211 | 0.00027768 | 0.00015901 | 9.0353e-05 | 5.059e-05 | 2.7226e-05 | 0 | 0 | 11 | 723.5367 | 808.6298 | 863.9956 | 925.5924 | 993.4883 | 1065.2904 | 1135.9002 | 1198.1211 | 1244.6163 | 1271.2166 | 1280.2155 | 1280.3919 | 1280.4969 | 1280.559 | 1280.5954 | 1280.6166 | 1280.6289 | 1280.636 | 1280.6401 | 1280.6423 | 1280.6421
11.1 | -4.2323 | -4.3439 | -4.0909 | -3.7187 | -3.2319 | -2.6474 | -2.0005 | -1.3488 | -0.76745 | -0.33074 | -0.081281 | 0.0014293 | 0.00083249 | 0.00048217 | 0.00027781 | 0.00015924 | 9.0783e-05 | 5.1378e-05 | 2.8669e-05 | 1.5397e-05 | 0 | 0 | 11.1 | 723.5367 | 786.1962 | 827.9691 | 876.7893 | 933.9019 | 998.7992 | 1068.6368 | 1137.9822 | 1199.4018 | 1245.3962 | 1271.6871 | 1280.4969 | 1280.559 | 1280.5954 | 1280.6166 | 1280.629 | 1280.6361 | 1280.6401 | 1280.6424 | 1280.6437 | 1280.6436
11.2 | -4.5894 | -4.6638 | -4.4669 | -4.1708 | -3.7697 | -3.2641 | -2.6674 | -2.0128 | -1.3563 | -0.77197 | -0.33345 | -0.082887 | 0.00048219 | 0.00027784 | 0.00015931 | 9.091e-05 | 5.1612e-05 | 2.9099e-05 | 1.6186e-05 | 8.6754e-06 | 0 | 0 | 11.2 | 723.5367 | 768.404 | 798.9899 | 836.2787 | 882.1002 | 937.2483 | 1000.8812 | 1069.9175 | 1138.7621 | 1199.8723 | 1245.6776 | 1271.8542 | 1280.5954 | 1280.6167 | 1280.629 | 1280.6361 | 1280.6402 | 1280.6425 | 1280.6438 | 1280.6445 | 1280.6445
11.3 | -4.8423 | -4.891 | -4.7437 | -4.518 | -4.203 | -3.7898 | -3.2764 | -2.6749 | -2.0173 | -1.359 | -0.77358 | -0.3344 | -0.083442 | 0.00015933 | 9.0947e-05 | 5.1681e-05 | 2.9226e-05 | 1.6419e-05 | 9.1052e-06 | 4.8712e-06 | 0 | 0 | 11.3 | 723.5367 | 754.8962 | 776.7135 | 804.3008 | 839.6251 | 884.1822 | 938.5291 | 1001.6611 | 1070.388 | 1139.0435 | 1200.0394 | 1245.7761 | 1271.9118 | 1280.629 | 1280.6361 | 1280.6402 | 1280.6425 | 1280.6438 | 1280.6446 | 1280.645 | 1280.6449
11.4 | -5.0175 | -5.0487 | -4.9421 | -4.7759 | -4.538 | -4.2153 | -3.7973 | -3.281 | -2.6776 | -2.0189 | -1.36 | -0.77413 | -0.33472 | -0.083629 | 5.1701e-05 | 2.9263e-05 | 1.6488e-05 | 9.2319e-06 | 5.1049e-06 | 2.7262e-06 | 0 | 0 | 11.4 | 723.5367 | 744.997 | 760.2071 | 780.0599 | 806.3828 | 840.9058 | 884.962 | 938.9996 | 1001.9425 | 1070.5551 | 1139.142 | 1200.097 | 1245.8097 | 1271.9313 | 1280.6402 | 1280.6425 | 1280.6438 | 1280.6446 | 1280.645 | 1280.6452 | 1280.6452
11.5 | -5.1363 | -5.1561 | -5.0809 | -4.9621 | -4.7882 | -4.5455 | -4.2199 | -3.8 | -3.2826 | -2.6786 | -2.0195 | -1.3603 | -0.77432 | -0.33483 | -0.083691 | 1.6508e-05 | 9.269e-06 | 5.1735e-06 | 2.853e-06 | 1.5211e-06 | 0 | 0 | 11.5 | 723.5367 | 737.952 | 748.3434 | 762.2891 | 781.3407 | 807.1627 | 841.3763 | 885.2435 | 939.1666 | 1002.041 | 1070.6128 | 1139.1756 | 1200.1165 | 1245.8209 | 1271.9377 | 1280.6438 | 1280.6446 | 1280.645 | 1280.6452 | 1280.6454 | 1280.6454
11.6 | -5.2155 | -5.2279 | -5.1761 | -5.0932 | -4.9696 | -4.7927 | -4.5482 | -4.2215 | -3.8009 | -3.2831 | -2.6789 | -2.0197 | -1.3604 | -0.77438 | -0.33486 | -0.083711 | 5.1935e-06 | 2.89e-06 | 1.5897e-06 | 8.4618e-07 | 0 | 0 | 11.6 | 723.5367 | 733.0611 | 740.034 | 749.6242 | 763.069 | 781.8112 | 807.4441 | 841.5434 | 885.342 | 939.2243 | 1002.0746 | 1070.6322 | 1139.1868 | 1200.1229 | 1245.8245 | 1271.9398 | 1280.645 | 1280.6452 | 1280.6454 | 1280.6454 | 1280.6454
11.7 | -5.2675 | -5.2752 | -5.2402 | -5.1836 | -5.0978 | -4.9723 | -4.7943 | -4.5492 | -4.222 | -3.8012 | -3.2833 | -2.679 | -2.0197 | -1.3604 | -0.7744 | -0.33487 | -0.083717 | 1.6097e-06 | 8.8324e-07 | 4.6943e-07 | 0 | 0 | 11.7 | 723.5367 | 729.7374 | 734.3419 | 740.8139 | 750.0947 | 763.3504 | 781.9782 | 807.5426 | 841.6011 | 885.3755 | 939.2437 | 1002.0858 | 1070.6386 | 1139.1904 | 1200.1249 | 1245.8257 | 1271.9404 | 1280.6454 | 1280.6454 | 1280.6455 | 1280.6455
11.8 | -5.3012 | -5.3058 | -5.2827 | -5.2448 | -5.1863 | -5.0994 | -4.9733 | -4.7949 | -4.5495 | -4.2222 | -3.8014 | -3.2834 | -2.679 | -2.0197 | -1.3604 | -0.77441 | -0.33488 | -0.083719 | 4.8941e-07 | 2.5974e-07 | 0 | 0 | 11.8 | 723.5367 | 727.5204 | 730.5173 | 734.8123 | 741.0953 | 750.2617 | 763.4489 | 782.0359 | 807.5761 | 841.6205 | 885.3867 | 939.2501 | 1002.0894 | 1070.6407 | 1139.1916 | 1200.1256 | 1245.8261 | 1271.9406 | 1280.6455 | 1280.6455 | 1280.6455
11.9 | -5.3227 | -5.3255 | -5.3104 | -5.2854 | -5.2464 | -5.1873 | -5.0999 | -4.9736 | -4.7951 | -4.5496 | -4.2223 | -3.8014 | -3.2834 | -2.679 | -2.0197 | -1.3604 | -0.77441 | -0.33488 | -0.08372 | 1.4336e-07 | 0 | 0 | 11.9 | 723.5367 | 726.0655 | 727.9908 | 730.7987 | 734.9794 | 741.1938 | 750.3194 | 763.4825 | 782.0553 | 807.5873 | 841.6269 | 885.3904 | 939.2522 | 1002.0906 | 1070.6413 | 1139.192 | 1200.1258 | 1245.8262 | 1271.9407 | 1280.6455 | 1280.6455
12 | -5.3362 | -5.3379 | -5.3282 | -5.312 | -5.2863 | -5.2469 | -5.1876 | -5.1001 | -4.9737 | -4.7951 | -4.5496 | -4.2223 | -3.8014 | -3.2834 | -2.679 | -2.0197 | -1.3604 | -0.77441 | -0.33488 | -0.08372 | 0 | 0 | 12 | 723.5367 | 725.1246 | 726.3469 | 728.1579 | 730.8972 | 735.0371 | 741.2274 | 750.3388 | 763.4937 | 782.0618 | 807.591 | 841.629 | 885.3915 | 939.2529 | 1002.091 | 1070.6416 | 1139.1921 | 1200.1259 | 1245.8262 | 1271.9407 | 1280.6455
12.1 | -5.3447 | -5.3457 | -5.3395 | -5.3291 | -5.3125 | -5.2866 | -5.2471 | -5.1877 | -5.1002 | -4.9737 | -4.7952 | -4.5496 | -4.2223 | -3.8014 | -3.2834 | -2.679 | -2.0197 | -1.3604 | -0.77441 | -0.33488 | 0 | 0 | 12.1 | 723.5367 | 724.5239 | 725.2916 | 726.4454 | 728.2156 | 730.9308 | 735.0565 | 741.2386 | 750.3452 | 763.4973 | 782.0638 | 807.5922 | 841.6296 | 885.3919 | 939.2531 | 1002.0911 | 1070.6416 | 1139.1921 | 1200.1259 | 1245.8262 | 1271.9407
12.2 | -5.35 | -5.3506 | -5.3467 | -5.3401 | -5.3295 | -5.3127 | -5.2868 | -5.2472 | -5.1878 | -5.1002 | -4.9737 | -4.7952 | -4.5497 | -4.2223 | -3.8014 | -3.2834 | -2.679 | -2.0197 | -1.3604 | -0.73255 | 0 | 0 | 12.2 | 723.5367 | 724.1449 | 724.6224 | 725.3493 | 726.479 | 728.235 | 730.942 | 735.0629 | 741.2422 | 750.3473 | 763.4985 | 782.0645 | 807.5925 | 841.6298 | 885.392 | 939.2532 | 1002.0911 | 1070.6416 | 1139.1921 | 1195.7735 | 1241.4738
12.3 | -5.3532 | -5.3535 | -5.3511 | -5.347 | -5.3403 | -5.3296 | -5.3128 | -5.2868 | -5.2472 | -5.1878 | -5.1002 | -4.9737 | -4.7952 | -4.5497 | -4.2223 | -3.8014 | -3.2834 | -2.679 | -1.9779 | -1.1721 | 0 | 0 | 12.3 | 723.5367 | 723.9083 | 724.2026 | 724.6559 | 725.3687 | 726.4902 | 728.2414 | 730.9456 | 735.065 | 741.2434 | 750.348 | 763.4989 | 782.0647 | 807.5927 | 841.6299 | 885.3921 | 939.2532 | 1002.0911 | 1066.2892 | 1119.6063 | 1180.5401
12.4 | -5.3551 | -5.3554 | -5.3539 | -5.3513 | -5.3471 | -5.3403 | -5.3296 | -5.3128 | -5.2868 | -5.2472 | -5.1878 | -5.1002 | -4.9737 | -4.7952 | -4.5497 | -4.2223 | -3.8014 | -3.2415 | -2.4907 | -1.5384 | 0 | 0 | 12.4 | 723.5367 | 723.762 | 723.9418 | 724.222 | 724.6671 | 725.3752 | 726.4938 | 728.2435 | 730.9468 | 735.0657 | 741.2438 | 750.3482 | 763.499 | 782.0648 | 807.5927 | 841.6299 | 885.3921 | 934.9008 | 982.5053 | 1020.5889 | 1089.1394
12.5 | -5.3563 | -5.3565 | -5.3555 | -5.354 | -5.3514 | -5.3471 | -5.3404 | -5.3296 | -5.3128 | -5.2868 | -5.2472 | -5.1878 | -5.1002 | -4.9737 | -4.7952 | -4.5497 | -4.1804 | -3.613 | -2.802 | -1.7581 | 0 | 0 | 12.5 | 723.5367 | 723.6723 | 723.7814 | 723.953 | 724.2284 | 724.6708 | 725.3772 | 726.495 | 728.2442 | 730.9472 | 735.0659 | 741.2439 | 750.3483 | 763.499 | 782.0648 | 807.5927 | 837.2775 | 865.8062 | 889.2004 | 906.3381 | 974.8886
12.6 | -5.357 | -5.3571 | -5.3566 | -5.3556 | -5.354 | -5.3514 | -5.3471 | -5.3404 | -5.3296 | -5.3128 | -5.2868 | -5.2472 | -5.1878 | -5.1002 | -4.9737 | -4.7533 | -4.3613 | -3.7409 | -2.8805 | -1.8131 | 0 | 0 | 12.6 | 723.5367 | 723.6178 | 723.6835 | 723.7878 | 723.9567 | 724.2305 | 724.672 | 725.3779 | 726.4954 | 728.2444 | 730.9473 | 735.0659 | 741.2439 | 750.3483 | 763.499 | 777.7124 | 788.0069 | 791.5772 | 789.639 | 786.3747 | 849.2127
12.7 | -5.3575 | -5.3575 | -5.3572 | -5.3566 | -5.3556 | -5.354 | -5.3514 | -5.3472 | -5.3404 | -5.3296 | -5.3128 | -5.2868 | -5.2472 | -5.1878 | -5.0584 | -4.7854 | -4.3138 | -3.6287 | -2.752 | -1.7267 | 0 | 0 | 12.7 | 723.5367 | 723.5849 | 723.6242 | 723.6872 | 723.7899 | 723.9579 | 724.2311 | 724.6723 | 725.3781 | 726.4955 | 728.2444 | 730.9473 | 735.066 | 741.2439 | 745.9959 | 743.9132 | 732.0121 | 711.8396 | 688.7515 | 669.6756 | 723.5367
12.8 | -5.3577 | -5.3577 | -5.3575 | -5.3572 | -5.3566 | -5.3556 | -5.354 | -5.3514 | -5.3472 | -5.3404 | -5.3296 | -5.3128 | -5.2868 | -5.2053 | -4.9994 | -4.6188 | -4.0528 | -3.3248 | -2.475 | -1.5433 | 0 | 0 | 12.8 | 723.5367 | 723.5652 | 723.5886 | 723.6263 | 723.6883 | 723.7906 | 723.9582 | 724.2313 | 724.6725 | 725.3782 | 726.4955 | 728.2445 | 730.9473 | 730.7136 | 721.6581 | 700.2955 | 667.746 | 629.1863 | 591.8763 | 563.0755 | 606.8377
12.9 | -5.3579 | -5.3579 | -5.3578 | -5.3576 | -5.3572 | -5.3566 | -5.3556 | -5.354 | -5.3514 | -5.3472 | -5.3404 | -5.3296 | -5.2709 | -5.0984 | -4.7658 | -4.2669 | -3.6299 | -2.899 | -2.1161 | -1.3094 | 0 | 0 | 12.9 | 723.5367 | 723.5535 | 723.5673 | 723.5897 | 723.627 | 723.6887 | 723.7908 | 723.9584 | 724.2314 | 724.6725 | 725.3782 | 726.4956 | 723.8921 | 711.3615 | 685.0132 | 645.4909 | 597.4698 | 547.7826 | 503.5104 | 470.6888 | 504.726
13 | -5.358 | -5.358 | -5.3579 | -5.3578 | -5.3576 | -5.3572 | -5.3566 | -5.3556 | -5.354 | -5.3514 | -5.3472 | -5.2985 | -5.1412 | -4.8314 | -4.3659 | -3.7769 | -3.1131 | -2.4212 | -1.7335 | -1.0639 | 0 | 0 | 13 | 723.5367 | 723.5465 | 723.5546 | 723.5679 | 723.5901 | 723.6272 | 723.6888 | 723.7908 | 723.9584 | 724.2314 | 724.6725 | 721.0258 | 706.9097 | 678.1917 | 635.1943 | 582.1875 | 525.5275 | 471.7939 | 426.5951 | 394.105 | 419.6329
13.1 | -5.358 | -5.358 | -5.358 | -5.3579 | -5.3578 | -5.3576 | -5.3572 | -5.3566 | -5.3556 | -5.354 | -5.3095 | -5.1588 | -4.859 | -4.4087 | -3.8425 | -3.2121 | -2.5682 | -1.9476 | -1.369 | -0.83327 | 0 | 0 | 13.1 | 723.5367 | 723.5424 | 723.5472 | 723.555 | 723.5682 | 723.5902 | 723.6272 | 723.6889 | 723.7908 | 723.9584 | 719.879 | 705.0866 | 675.3255 | 630.7425 | 575.366 | 515.2309 | 456.5116 | 404.34 | 362.3885 | 332.9927 | 351.5585
13.2 | -5.358 | -5.358 | -5.358 | -5.358 | -5.3579 | -5.3578 | -5.3576 | -5.3572 | -5.3566 | -5.3138 | -5.1657 | -4.87 | -4.4262 | -3.87 | -3.2549 | -2.6338 | -2.0466 | -1.5159 | -1.0473 | -0.6324 | 0 | 0 | 13.2 | 723.5367 | 723.54 | 723.5428 | 723.5474 | 723.5551 | 723.5682 | 723.5903 | 723.6272 | 723.6889 | 719.4384 | 704.3725 | 674.1787 | 628.9194 | 572.4997 | 510.7791 | 449.6901 | 394.0434 | 347.1062 | 310.7376 | 285.8048 | 298.9555
13.3 | -5.3581 | -5.3581 | -5.358 | -5.358 | -5.358 | -5.3579 | -5.3578 | -5.3576 | -5.3153 | -5.1682 | -4.8742 | -4.4331 | -3.8811 | -3.2725 | -2.6613 | -2.0894 | -1.5815 | -1.1463 | -0.77938 | -0.467 | 0 | 0 | 13.3 | 723.5367 | 723.5387 | 723.5403 | 723.5429 | 723.5475 | 723.5552 | 723.5682 | 723.5903 | 719.2748 | 704.103 | 673.7381 | 628.2053 | 571.353 | 508.9561 | 446.8238 | 389.5916 | 340.2847 | 300.441 | 270.5224 | 250.3989 | 259.5033
13.4 | -5.3581 | -5.3581 | -5.3581 | -5.358 | -5.358 | -5.358 | -5.3579 | -5.3159 | -5.1692 | -4.8758 | -4.4357 | -3.8853 | -3.2793 | -2.6724 | -2.1069 | -1.6091 | -1.1892 | -0.84498 | -0.56603 | -0.3367 | 0 | 0 | 13.4 | 723.5367 | 723.5378 | 723.5388 | 723.5403 | 723.543 | 723.5475 | 723.5552 | 719.2158 | 704.0044 | 673.5745 | 627.9358 | 570.9124 | 508.242 | 445.677 | 387.7686 | 337.4184 | 295.9893 | 263.7009 | 240.1023 | 224.4948 | 230.6728
13.5 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.358 | -5.358 | -5.3161 | -5.1695 | -4.8764 | -4.4366 | -3.8869 | -3.2819 | -2.6766 | -2.1138 | -1.6201 | -1.2067 | -0.87255 | -0.60884 | -0.40231 | -0.23767 | 0 | 0 | 13.5 | 723.5367 | 723.5374 | 723.5379 | 723.5388 | 723.5403 | 723.543 | 719.1951 | 703.9693 | 673.5155 | 627.8372 | 570.7488 | 507.9724 | 445.2365 | 387.0545 | 336.2717 | 294.1662 | 260.8347 | 235.6505 | 217.6733 | 205.961 | 210.0796
13.6 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3162 | -5.1696 | -4.8766 | -4.437 | -3.8874 | -3.2829 | -2.6782 | -2.1164 | -1.6244 | -1.2136 | -0.88358 | -0.62638 | -0.42987 | -0.28049 | -0.16464 | 0 | 0 | 13.6 | 723.5367 | 723.5371 | 723.5374 | 723.5379 | 723.5388 | 719.1879 | 703.9571 | 673.4947 | 627.8021 | 570.6898 | 507.8738 | 445.0729 | 386.7849 | 335.8311 | 293.4521 | 259.6879 | 233.8275 | 214.8071 | 201.5092 | 192.9615 | 195.6643
13.7 | -5.3581 | -5.3581 | -5.3581 | -5.3581 | -5.3162 | -5.1697 | -4.8767 | -4.4371 | -3.8876 | -3.2832 | -2.6787 | -2.1173 | -1.6259 | -1.2162 | -0.88782 | -0.63325 | -0.4409 | -0.29802 | -0.1922 | -0.11214 | 0 | 0 | 13.7 | 723.5367 | 723.537 | 723.5371 | 723.5374 | 719.1855 | 703.953 | 673.4876 | 627.7899 | 570.669 | 507.8387 | 445.0138 | 386.6864 | 335.6675 | 293.1826 | 259.2473 | 233.1134 | 213.6603 | 199.6861 | 190.0952 | 184.005 | 185.7539
13.8 | -5.3581 | -5.3581 | -5.3581 | -5.3162 | -5.1697 | -4.8767 | -4.4371 | -3.8877 | -3.2833 | -2.6789 | -2.1177 | -1.6265 | -1.2171 | -0.88939 | -0.63584 | -0.44514 | -0.30489 | -0.20323 | -0.12967 | -0.075224 | 0 | 0 | 13.8 | 723.5367 | 723.5369 | 723.537 | 719.1847 | 703.9516 | 673.4852 | 627.7857 | 570.6619 | 507.8265 | 444.9931 | 386.6513 | 335.6085 | 293.084 | 259.0837 | 232.8439 | 213.2197 | 198.972 | 188.9485 | 182.1819 | 177.9324 | 179.0497
13.9 | -5.3581 | -5.3581 | -5.3162 | -5.1697 | -4.8767 | -4.4371 | -3.8877 | -3.2834 | -2.679 | -2.1178 | -1.6267 | -1.2174 | -0.88996 | -0.63679 | -0.44671 | -0.30748 | -0.20747 | -0.13654 | -0.086254 | -0.049773 | 0 | 0 | 13.9 | 723.5367 | 723.5368 | 719.1845 | 703.9511 | 673.4844 | 627.7844 | 570.6594 | 507.8224 | 444.9859 | 386.6391 | 335.5877 | 293.0489 | 259.0247 | 232.7453 | 213.0561 | 198.7025 | 188.5079 | 181.4678 | 176.7856 | 173.8746 | 174.5803
14 | -5.3581 | -5.3162 | -5.1697 | -4.8767 | -4.4372 | -3.8877 | -3.2834 | -2.679 | -2.1178 | -1.6268 | -1.2176 | -0.89016 | -0.63712 | -0.44728 | -0.30843 | -0.20904 | -0.13913 | -0.090491 | -0.056641 | -0.032522 | 0 | 0 | 14 | 723.5367 | 719.1844 | 703.951 | 673.4841 | 627.7839 | 570.6586 | 507.821 | 444.9835 | 386.6349 | 335.5806 | 293.0367 | 259.004 | 232.7102 | 212.9971 | 198.6039 | 188.3443 | 181.1983 | 176.345 | 173.1605 | 171.1988 | 171.6399

## case b)
HYDRAULIC MODELLING | [22 empty] | ADAM BABULJAK
WATER HAMMER CALCULATIONS
INPUT VALUES
t | 14 | s | time of simulation
Q | 30 | m/s | initial discharge
D | 2.67 | m | pipe diameter
H0 | 725 | m | reservoir level
e | 0.03 | m | pipe wall thickness
E | 196200000000 | N/m2 | pipe elasticity module
K | 1962000000 | N/m2 | water compressibility
θ | 0 | - | pipe inclination
L | 2040 | m | pipe length
4) velocity of water hammer propagation
|  |  | a = | 1018.8696 | m/s | ≈ | 1020 | m/s
5) Maximum pressure in the systém
v0 = | 5.3581 | m/s
ΔHmax = | 556.4914 | m
Hmax = | 1281.4914 | m
Hmin = | 168.5086 | m
WATER HAMMER CALCULATION
lambda | 0.032 | [-] | [5 empty] | D = | 2.67 | m
tclose | 0 | s | [5 empty] | a = | 1020 | m/s
M | 21 | [-] | [5 empty] | H0 = | 725 | m
N | 20 | [-] | [5 empty] | Δx | 102 | m
t | 14 | s | [5 empty] | Δt | 0.1 | s
INITIAL CONTITIONS:
INTERNAL POINTS CALCULATION
velocity [m/s] | A | [9 empty] | B | [9 empty] | C |  | head [m] | A | [9 empty] | B | [9 empty] | C
Li = | 0 | 102 | 204 | 306 | 408 | 510 | 612 | 714 | 816 | 918 | 1020 | 1122 | 1224 | 1326 | 1428 | 1530 | 1632 | 1734 | 1836 | 1938 | 2040 |  | Li = | 0 | 102 | 204 | 306 | 408 | 510 | 612 | 714 | 816 | 918 | 1020 | 1122 | 1224 | 1326 | 1428 | 1530 | 1632 | 1734 | 1836 | 1938 | 2040
profile i | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 |  | profile | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 11
t | [21 empty] | τ | t
0 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 1 | 0 | 723.5367 | 721.748 | 719.9592 | 718.1704 | 716.3816 | 714.5928 | 712.8041 | 711.0153 | 709.2265 | 707.4377 | 705.6489 | 703.8601 | 702.0714 | 700.2826 | 698.4938 | 696.705 | 694.9162 | 693.1274 | 691.3387 | 689.5499 | 687.7611
0.1 | 5.3495 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 0 | 0 | 0.1 | 723.5367 | 721.748 | 719.9592 | 718.1704 | 716.3816 | 714.5928 | 712.8041 | 711.0153 | 709.2265 | 707.4377 | 705.6489 | 703.8601 | 702.0714 | 700.2826 | 698.4938 | 696.705 | 694.9162 | 693.1274 | 691.3387 | 689.5499 | 688.6555
0.2 | 5.3452 | 5.3538 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 2.6833 | 0 | 0 | 0.2 | 723.5367 | 721.3008 | 719.9592 | 718.1704 | 716.3816 | 714.5928 | 712.8041 | 711.0153 | 709.2265 | 707.4377 | 705.6489 | 703.8601 | 702.0714 | 700.2826 | 698.4938 | 696.705 | 694.9162 | 693.1274 | 691.3387 | 968.5506 | 967.6562
0.3 | 5.3431 | 5.3517 | 5.3538 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 2.6855 | 1.3417 | 0 | 0 | 0.3 | 723.5367 | 721.0786 | 719.5134 | 718.1704 | 716.3816 | 714.5928 | 712.8041 | 711.0153 | 709.2265 | 707.4377 | 705.6489 | 703.8601 | 702.0714 | 700.2826 | 698.4938 | 696.705 | 694.9162 | 693.1274 | 969.892 | 1108.051 | 1107.604
0.4 | 5.3421 | 5.3507 | 5.3517 | 5.3538 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 2.6887 | 1.3454 | 0.67835 | 0 | 0 | 0.4 | 723.5367 | 720.969 | 719.292 | 717.7254 | 716.3816 | 714.5928 | 712.8041 | 711.0153 | 709.2265 | 707.4377 | 705.6489 | 703.8601 | 702.0714 | 700.2826 | 698.4938 | 696.705 | 694.9162 | 971.3454 | 1109.3922 | 1178.3602 | 1177.578
0.5 | 5.3416 | 5.3502 | 5.3507 | 5.3517 | 5.3538 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 2.6919 | 1.3495 | 0.68573 | 0.34428 | 0 | 0 | 0.5 | 723.5367 | 720.9152 | 719.1834 | 717.5043 | 715.9373 | 714.5928 | 712.8041 | 711.0153 | 709.2265 | 707.4377 | 705.6489 | 703.8601 | 702.0714 | 700.2826 | 698.4938 | 696.705 | 972.799 | 1110.7614 | 1179.3667 | 1213.4314 | 1213.235
0.6 | 5.3414 | 5.3499 | 5.3502 | 5.3507 | 5.3517 | 5.3538 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 2.6951 | 1.3535 | 0.69317 | 0.35257 | 0.17986 | 0 | 0 | 0.6 | 723.5367 | 720.8881 | 719.1301 | 717.3966 | 715.7165 | 714.1492 | 712.8041 | 711.0153 | 709.2265 | 707.4377 | 705.6489 | 703.8601 | 702.0714 | 700.2826 | 698.4938 | 974.2528 | 1112.1307 | 1180.3805 | 1214.3538 | 1231.9503 | 1231.2317
0.7 | 5.3413 | 5.3498 | 5.3499 | 5.3502 | 5.3507 | 5.3517 | 5.3538 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 2.6984 | 1.3575 | 0.7006 | 0.36088 | 0.18837 | 0.095087 | 0 | 0 | 0.7 | 723.5367 | 720.8752 | 719.1033 | 717.3437 | 715.6097 | 713.9288 | 712.3611 | 711.0153 | 709.2265 | 707.4377 | 705.6489 | 703.8601 | 702.0714 | 700.2826 | 975.707 | 1113.5003 | 1181.3947 | 1215.2782 | 1232.8513 | 1241.1223 | 1240.9413
0.8 | 5.3412 | 5.3498 | 5.3498 | 5.35 | 5.3502 | 5.3507 | 5.3517 | 5.3538 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 2.7016 | 1.3616 | 0.70804 | 0.36918 | 0.19688 | 0.10366 | 0.05527 | 0 | 0 | 0.8 | 723.5367 | 720.8683 | 719.0905 | 717.3171 | 715.5574 | 713.8229 | 712.1411 | 710.5731 | 709.2265 | 707.4377 | 705.6489 | 703.8601 | 702.0714 | 977.1614 | 1114.87 | 1182.4093 | 1216.2029 | 1233.7529 | 1242.0182 | 1246.6891 | 1245.9752
0.9 | 5.3412 | 5.3498 | 5.3498 | 5.3499 | 5.35 | 5.3502 | 5.3507 | 5.3517 | 5.3538 | 5.3581 | 5.3581 | 5.3581 | 2.7048 | 1.3656 | 0.71546 | 0.37748 | 0.20539 | 0.11224 | 0.063856 | 0.032799 | 0 | 0 | 0.9 | 723.5367 | 720.8654 | 719.0837 | 717.3044 | 715.5309 | 713.7709 | 712.036 | 710.3534 | 708.785 | 707.4377 | 705.6489 | 703.8601 | 978.6161 | 1116.2399 | 1183.4244 | 1217.1278 | 1234.6548 | 1242.9144 | 1247.5832 | 1249.3859 | 1249.2055
1 | 5.3412 | 5.3498 | 5.3498 | 5.3498 | 5.3499 | 5.35 | 5.3503 | 5.3508 | 5.3517 | 5.3539 | 5.3581 | 2.708 | 1.3696 | 0.72289 | 0.38578 | 0.2139 | 0.12081 | 0.072441 | 0.041394 | 0.024125 | 0 | 0 | 1 | 723.5367 | 720.8635 | 719.0808 | 717.2977 | 715.5183 | 713.7447 | 711.9845 | 710.2492 | 708.5657 | 706.9969 | 705.6489 | 980.071 | 1117.6099 | 1184.4399 | 1218.053 | 1235.5569 | 1243.8106 | 1248.4773 | 1250.2799 | 1251.7141 | 1251.0008
1.1 | 5.3412 | 5.3498 | 5.3498 | 5.3498 | 5.3499 | 5.3499 | 5.35 | 5.3503 | 5.3508 | 5.3518 | 2.707 | 1.3736 | 0.73031 | 0.39407 | 0.22241 | 0.12938 | 0.081026 | 0.049987 | 0.032716 | 0.017229 | 0 | 0 | 1.1 | 723.5367 | 720.863 | 719.0789 | 717.2948 | 715.5116 | 713.7322 | 711.9585 | 710.1981 | 708.4623 | 706.7779 | 981.0862 | 1118.9802 | 1185.4559 | 1218.9785 | 1236.4592 | 1244.707 | 1249.3715 | 1251.1739 | 1252.6075 | 1252.7923 | 1252.6117
1.2 | 5.3413 | 5.3498 | 5.3498 | 5.3498 | 5.3499 | 5.3499 | 5.3499 | 5.3501 | 5.3503 | 2.7071 | 1.3713 | 0.7335 | 0.40237 | 0.23092 | 0.13795 | 0.08961 | 0.05858 | 0.041307 | 0.025825 | 0.016338 | 0 | 0 | 1.2 | 723.5367 | 720.8623 | 719.0784 | 717.2929 | 715.5088 | 713.7256 | 711.9461 | 710.1723 | 708.4117 | 982.2195 | 1119.6919 | 1186.0329 | 1219.9042 | 1237.3618 | 1245.6035 | 1250.2657 | 1252.068 | 1253.501 | 1253.6861 | 1254.3104 | 1253.5977
1.3 | 5.3413 | 5.3499 | 5.3499 | 5.3499 | 5.3499 | 5.3499 | 5.3499 | 5.35 | 2.7096 | 1.3739 | 0.73784 | 0.40433 | 0.2352 | 0.14652 | 0.098193 | 0.067173 | 0.049898 | 0.03442 | 0.02493 | 0.013337 | 0 | 0 | 1.3 | 723.5367 | 720.8624 | 719.0777 | 717.2924 | 715.5069 | 713.7227 | 711.9395 | 710.16 | 983.5975 | 1120.9087 | 1186.7288 | 1220.1726 | 1237.8255 | 1246.5001 | 1251.1601 | 1252.9621 | 1254.3945 | 1254.5799 | 1255.2038 | 1254.9845 | 1254.8034
1.4 | 5.3413 | 5.3499 | 5.3499 | 5.3499 | 5.3499 | 5.3499 | 5.3499 | 2.7126 | 1.3776 | 0.74453 | 0.41116 | 0.24063 | 0.14877 | 0.10255 | 0.075765 | 0.058488 | 0.043015 | 0.033521 | 0.021933 | 0.01439 | 0 | 0 | 1.4 | 723.5367 | 720.862 | 719.0778 | 717.2917 | 715.5064 | 713.7209 | 711.9367 | 985.0326 | 1122.2401 | 1187.6695 | 1220.9464 | 1238.4082 | 1246.7395 | 1251.6156 | 1253.8563 | 1255.288 | 1255.4738 | 1256.0972 | 1255.8782 | 1256.2997 | 1255.5873
1.5 | 5.3413 | 5.3499 | 5.3499 | 5.3499 | 5.3499 | 5.3499 | 2.7158 | 1.3815 | 0.75176 | 0.41909 | 0.2484 | 0.15587 | 0.10806 | 0.078035 | 0.062857 | 0.051609 | 0.042112 | 0.030528 | 0.022982 | 0.012365 | 0 | 0 | 1.5 | 723.5367 | 720.8622 | 719.0774 | 717.2918 | 715.5057 | 713.7204 | 986.4822 | 1123.5999 | 1188.6675 | 1221.8349 | 1239.2354 | 1247.4843 | 1252.1899 | 1254.0932 | 1255.7427 | 1256.3676 | 1256.9906 | 1256.772 | 1257.193 | 1256.873 | 1256.6916
1.6 | 5.3414 | 5.3499 | 5.3499 | 5.3499 | 5.3499 | 2.719 | 1.3855 | 0.75912 | 0.42729 | 0.25672 | 0.16408 | 0.11591 | 0.085165 | 0.068368 | 0.053882 | 0.046482 | 0.039123 | 0.031573 | 0.020961 | 0.013902 | 0 | 0 | 1.6 | 723.5367 | 720.8619 | 719.0776 | 717.2914 | 715.5058 | 987.9355 | 1124.9669 | 1189.6801 | 1222.7519 | 1240.1199 | 1248.3435 | 1253.0087 | 1254.8354 | 1256.3162 | 1256.6042 | 1257.4451 | 1257.6658 | 1258.0864 | 1257.7668 | 1258.1371 | 1257.4252
1.7 | 5.3414 | 5.35 | 5.35 | 5.35 | 2.7222 | 1.3895 | 0.76651 | 0.43555 | 0.26517 | 0.17255 | 0.12431 | 0.093393 | 0.076229 | 0.061015 | 0.051994 | 0.041396 | 0.035943 | 0.029555 | 0.022493 | 0.012123 | 0 | 0 | 1.7 | 723.5367 | 720.8622 | 719.0773 | 717.2916 | 989.3899 | 1126.3358 | 1190.6966 | 1223.6762 | 1241.0186 | 1249.2312 | 1253.8845 | 1255.692 | 1257.1341 | 1257.3461 | 1258.0185 | 1257.9023 | 1258.5408 | 1258.6605 | 1259.0304 | 1258.6857 | 1258.5038
1.8 | 5.3414 | 5.35 | 5.35 | 2.7254 | 1.3936 | 0.7739 | 0.44382 | 0.27365 | 0.18109 | 0.13284 | 0.10189 | 0.084636 | 0.069246 | 0.059856 | 0.048529 | 0.041455 | 0.031829 | 0.026863 | 0.020718 | 0.013778 | 0 | 0 | 1.8 | 723.5367 | 720.8619 | 719.0776 | 990.8448 | 1127.7053 | 1191.7144 | 1224.6025 | 1241.9211 | 1250.1261 | 1254.7745 | 1256.577 | 1258.009 | 1258.2024 | 1258.8362 | 1258.6441 | 1259.1141 | 1258.897 | 1259.4848 | 1259.5794 | 1259.9365 | 1259.225
1.9 | 5.3414 | 5.35 | 2.7286 | 1.3976 | 0.78129 | 0.45209 | 0.28214 | 0.18965 | 0.14141 | 0.11046 | 0.093179 | 0.077749 | 0.068265 | 0.056761 | 0.049318 | 0.038962 | 0.032376 | 0.022991 | 0.018149 | 0.012063 | 0 | 0 | 1.9 | 723.5367 | 720.8622 | 992.3001 | 1129.0751 | 1192.7328 | 1225.5295 | 1242.8246 | 1251.0228 | 1255.6681 | 1257.469 | 1258.898 | 1259.087 | 1259.7109 | 1259.5003 | 1259.9318 | 1259.6388 | 1260.0581 | 1259.8158 | 1260.3909 | 1260.4792 | 1260.297
2 | 5.3415 | 2.7318 | 1.4016 | 0.78868 | 0.46037 | 0.29063 | 0.19821 | 0.14998 | 0.11904 | 0.10175 | 0.086318 | 0.076809 | 0.065265 | 0.057727 | 0.047194 | 0.040238 | 0.030125 | 0.023661 | 0.014337 | 0.0095255 | 0 | 0 | 2 | 723.5367 | 993.7542 | 1130.4451 | 1193.7518 | 1226.4569 | 1243.7286 | 1251.92 | 1256.5626 | 1258.3628 | 1259.7905 | 1259.9785 | 1260.5996 | 1260.3847 | 1260.8064 | 1260.4948 | 1260.8757 | 1260.5576 | 1260.9641 | 1260.7157 | 1261.2875 | 1261.0153
2.1 | 2.7264 | 1.4057 | 0.79607 | 0.46864 | 0.29911 | 0.20676 | 0.15856 | 0.12763 | 0.11034 | 0.094903 | 0.085385 | 0.073835 | 0.066271 | 0.055698 | 0.048648 | 0.038357 | 0.031524 | 0.02147 | 0.015038 | 0.0057276 | 0 | 0 | 2.1 | 723.5367 | 1131.8139 | 1194.7712 | 1227.3846 | 1244.633 | 1252.8176 | 1257.4574 | 1259.2571 | 1260.6839 | 1260.8719 | 1261.4919 | 1261.2761 | 1261.695 | 1261.3792 | 1261.7502 | 1261.4136 | 1261.7817 | 1261.4574 | 1261.8607 | 1261.6108 | 1261.6466
2.2 | 0.099886 | -0.50726 | 0.47691 | 0.3076 | 0.21532 | 0.16713 | 0.13621 | 0.11892 | 0.10349 | 0.09397 | 0.082421 | 0.074848 | 0.064268 | 0.057192 | 0.046861 | 0.039933 | 0.029702 | 0.022901 | 0.012861 | 0.0085486 | 0 | 0 | 2.2 | 723.5367 | 1059.5086 | 1228.3126 | 1245.5375 | 1253.7153 | 1258.3524 | 1260.1516 | 1261.5775 | 1261.7656 | 1262.385 | 1262.1693 | 1262.5872 | 1262.2706 | 1262.6388 | 1262.2979 | 1262.6562 | 1262.3134 | 1262.6783 | 1262.3525 | 1262.5354 | 1261.9265
2.3 | -1.8192 | -2.1391 | -0.99436 | 0.22387 | 0.1757 | 0.1448 | 0.1275 | 0.11208 | 0.10255 | 0.09101 | 0.083432 | 0.072854 | 0.065769 | 0.055431 | 0.048478 | 0.038206 | 0.031311 | 0.021093 | 0.016411 | 0.0084794 | 0 | 0 | 2.3 | 723.5367 | 956.3243 | 1110.1606 | 1254.6133 | 1259.2475 | 1261.0462 | 1262.4713 | 1262.6596 | 1263.2784 | 1263.0629 | 1263.4802 | 1263.1636 | 1263.5309 | 1263.1892 | 1263.5448 | 1263.1977 | 1263.5527 | 1263.2085 | 1263.353 | 1262.8081 | 1262.6754
2.4 | -3.0962 | -3.2647 | -2.3907 | -1.126 | 0.15338 | 0.13609 | 0.12067 | 0.11114 | 0.0996 | 0.092018 | 0.081444 | 0.074353 | 0.064017 | 0.057055 | 0.046776 | 0.039855 | 0.029597 | 0.024821 | 0.016712 | 0.011464 | 0 | 0 | 2.4 | 723.5367 | 873.9652 | 982.6256 | 1123.8751 | 1261.9408 | 1263.3652 | 1263.5536 | 1264.1719 | 1263.9567 | 1264.3735 | 1264.0572 | 1264.4238 | 1264.0822 | 1264.4368 | 1264.0889 | 1264.4412 | 1264.0928 | 1264.2274 | 1263.6641 | 1263.8674 | 1263.1826
2.5 | -3.8978 | -3.9848 | -3.3935 | -2.4601 | -1.1654 | 0.12926 | 0.11972 | 0.10819 | 0.1006 | 0.090034 | 0.082939 | 0.072607 | 0.065639 | 0.055362 | 0.048432 | 0.038167 | 0.033365 | 0.025215 | 0.019874 | 0.010671 | 0 | 0 | 2.5 | 723.5367 | 816.4006 | 887.7319 | 990.0249 | 1128.0084 | 1264.4477 | 1265.0654 | 1264.8505 | 1265.2668 | 1264.9508 | 1265.317 | 1264.9757 | 1265.3296 | 1264.9819 | 1265.3332 | 1264.984 | 1265.1159 | 1264.5483 | 1264.7418 | 1264.2921 | 1264.121
2.6 | -4.3785 | -4.4272 | -4.0508 | -3.431 | -2.4833 | -1.1815 | 0.11678 | 0.10919 | 0.098623 | 0.091525 | 0.081197 | 0.074225 | 0.063952 | 0.057017 | 0.046754 | 0.041942 | 0.033786 | 0.028418 | 0.019175 | 0.012922 | 0 | 0 | 2.6 | 723.5367 | 779.4201 | 823.9497 | 892.0317 | 992.6211 | 1129.7287 | 1265.7444 | 1266.1602 | 1265.8445 | 1266.2102 | 1265.8692 | 1266.2227 | 1265.8753 | 1266.226 | 1265.8769 | 1266.0078 | 1265.4395 | 1265.6302 | 1265.1763 | 1265.4646 | 1264.7613
2.7 | -4.66 | -4.6869 | -4.4613 | -4.0714 | -3.4454 | -2.4948 | -1.1918 | 0.10721 | 0.10011 | 0.089786 | 0.082811 | 0.072542 | 0.065603 | 0.055343 | 0.050527 | 0.042372 | 0.036995 | 0.027745 | 0.021467 | 0.011583 | 0 | 0 | 2.7 | 723.5367 | 756.705 | 783.9354 | 826.7936 | 893.9317 | 994.0124 | 1130.8447 | 1266.7383 | 1267.1035 | 1266.7628 | 1267.1158 | 1266.7687 | 1267.119 | 1266.7702 | 1266.9006 | 1266.3323 | 1266.5221 | 1266.0675 | 1266.353 | 1265.9657 | 1265.7848
2.8 | -4.8198 | -4.8386 | -4.7046 | -4.4728 | -4.0804 | -3.4539 | -2.5034 | -1.2007 | 0.098375 | 0.091396 | 0.081132 | 0.074188 | 0.063933 | 0.059113 | 0.050962 | 0.04558 | 0.036332 | 0.030044 | 0.020153 | 0.013466 | 0 | 0 | 2.8 | 723.5367 | 743.4045 | 759.7514 | 786.119 | 828.4407 | 895.2314 | 995.1025 | 1131.8099 | 1267.6565 | 1268.009 | 1267.6623 | 1268.012 | 1267.6636 | 1267.7935 | 1267.2256 | 1267.4148 | 1266.9603 | 1267.2449 | 1266.8568 | 1267.1849 | 1266.4774
2.9 | -4.9108 | -4.9228 | -4.8481 | -4.7112 | -4.4784 | -4.0865 | -3.4609 | -2.5113 | -1.2092 | 0.08972 | 0.082773 | 0.072523 | 0.067699 | 0.059552 | 0.054166 | 0.044921 | 0.038628 | 0.02874 | 0.022043 | 0.011901 | 0 | 0 | 2.9 | 723.5367 | 735.6536 | 745.7413 | 761.6437 | 787.7066 | 829.7893 | 896.3818 | 996.1179 | 1132.7377 | 1268.5558 | 1268.9051 | 1268.557 | 1268.6865 | 1268.119 | 1268.3077 | 1267.8536 | 1268.1375 | 1267.7496 | 1268.0767 | 1267.7149 | 1267.5312
3 | -4.9606 | -4.9719 | -4.9281 | -4.852 | -4.7149 | -4.4827 | -4.0919 | -3.4676 | -2.519 | -1.2176 | 0.081112 | 0.076284 | 0.068141 | 0.062751 | 0.053511 | 0.047214 | 0.037329 | 0.030627 | 0.020487 | 0.013645 | 0 | 0 | 3 | 723.5367 | 731.3786 | 737.6483 | 747.5078 | 763.2394 | 789.1461 | 831.0642 | 897.4957 | 997.1151 | 1133.6564 | 1269.4505 | 1269.5795 | 1269.0123 | 1269.2007 | 1268.7469 | 1269.0304 | 1268.6428 | 1268.9694 | 1268.6076 | 1268.9499 | 1268.2417
3.1 | -4.9892 | -4.9975 | -4.9751 | -4.9306 | -4.8545 | -4.7178 | -4.4866 | -4.097 | -3.4742 | -2.5267 | -1.2238 | 0.07673 | 0.071336 | 0.062101 | 0.0558 | 0.045919 | 0.039213 | 0.029077 | 0.022229 | 0.012003 | 0 | 0 | 3.1 | 723.5367 | 728.9024 | 733.2082 | 739.3613 | 749.1268 | 764.7618 | 790.5496 | 832.3217 | 898.6012 | 998.1082 | 1134.3536 | 1269.9057 | 1270.0936 | 1269.6402 | 1269.9233 | 1269.5361 | 1269.8622 | 1269.5008 | 1269.8425 | 1269.4898 | 1269.3052
3.2 | -5.0042 | -5.0138 | -4.9996 | -4.9769 | -4.9324 | -4.8566 | -4.7206 | -4.4903 | -4.1021 | -3.4786 | -2.5301 | -1.2285 | 0.070689 | 0.064385 | 0.054509 | 0.047799 | 0.037667 | 0.030815 | 0.020593 | 0.013699 | 0 | 0 | 3.2 | 723.5367 | 727.6391 | 730.6524 | 734.8992 | 741.0011 | 750.7096 | 766.2666 | 791.945 | 833.5758 | 899.486 | 998.6624 | 1134.8909 | 1270.5335 | 1270.8162 | 1270.4294 | 1270.755 | 1270.394 | 1270.7353 | 1270.3829 | 1270.7295 | 1270.0215
3.3 | -5.0137 | -5.0211 | -5.0153 | -5.001 | -4.9783 | -4.9341 | -4.8587 | -4.7233 | -4.492 | -4.103 | -3.4815 | -2.5352 | -1.2353 | 0.063097 | 0.056384 | 0.046256 | 0.039401 | 0.029183 | 0.022284 | 0.012034 | 0 | 0 | 3.3 | 723.5367 | 726.854 | 729.3507 | 732.3345 | 736.554 | 742.6231 | 752.2839 | 767.7678 | 793.1199 | 834.3916 | 900.2115 | 999.3898 | 1135.6369 | 1271.3226 | 1271.6479 | 1271.2873 | 1271.6281 | 1271.2761 | 1271.6223 | 1271.2728 | 1271.0877
3.4 | -5.0183 | -5.0274 | -5.0224 | -5.0165 | -5.0022 | -4.9796 | -4.9356 | -4.8586 | -4.7218 | -4.4921 | -4.1056 | -3.4864 | -2.5418 | -1.243 | 0.054845 | 0.047986 | 0.037772 | 0.03087 | 0.020624 | 0.013713 | 0 | 0 | 3.4 | 723.5367 | 726.5265 | 728.5472 | 731.0296 | 733.9987 | 738.2001 | 744.2411 | 753.6378 | 768.831 | 794.136 | 835.3813 | 901.1462 | 1000.2788 | 1136.4921 | 1272.1805 | 1272.5209 | 1272.1693 | 1272.515 | 1272.166 | 1272.5135 | 1271.8059
3.5 | -5.0221 | -5.0293 | -5.0285 | -5.0235 | -5.0176 | -5.0034 | -4.9788 | -4.933 | -4.8569 | -4.722 | -4.4942 | -4.1097 | -3.4924 | -2.5491 | -1.2512 | 0.046361 | 0.039455 | 0.029214 | 0.022299 | 0.012044 | 0 | 0 | 3.5 | 723.5367 | 726.2547 | 728.2109 | 730.2249 | 732.6998 | 735.6588 | 739.6256 | 745.4213 | 754.8327 | 770.068 | 795.3612 | 836.5326 | 902.1904 | 1001.2369 | 1137.389 | 1273.0625 | 1273.4078 | 1273.0591 | 1273.4062 | 1273.0581 | 1272.8726
3.6 | -5.0236 | -5.0326 | -5.0303 | -5.0295 | -5.0245 | -5.0165 | -5.0003 | -4.9765 | -4.9321 | -4.8573 | -4.7237 | -4.4973 | -4.1144 | -3.4987 | -2.5566 | -1.2595 | 0.037803 | 0.030884 | 0.020633 | 0.013715 | 0 | 0 | 3.6 | 723.5367 | 726.2054 | 727.9349 | 729.8885 | 731.8984 | 734.1496 | 736.8814 | 740.8924 | 746.7751 | 756.2361 | 771.466 | 796.6956 | 837.7534 | 903.2768 | 1002.2196 | 1138.3 | 1273.9522 | 1274.2989 | 1273.9513 | 1274.2987 | 1273.5915
3.7 | -5.0258 | -5.033 | -5.0336 | -5.0313 | -5.0284 | -5.0213 | -5.014 | -4.999 | -4.9762 | -4.9326 | -4.8587 | -4.7261 | -4.5008 | -4.1193 | -3.5051 | -2.5641 | -1.2678 | 0.029222 | 0.022301 | 0.012047 | 0 | 0 | 3.7 | 723.5367 | 726.0842 | 727.8837 | 729.6125 | 731.346 | 733.135 | 735.4411 | 738.2778 | 742.3673 | 748.289 | 757.748 | 772.9327 | 798.0722 | 838.9993 | 904.3779 | 1003.2107 | 1139.2156 | 1274.8443 | 1275.1913 | 1274.844 | 1274.6581
3.8 | -5.0265 | -5.0354 | -5.0339 | -5.0325 | -5.0281 | -5.0258 | -5.0198 | -5.0135 | -4.9992 | -4.9769 | -4.9339 | -4.8605 | -4.7286 | -4.5044 | -4.1243 | -3.5116 | -2.5717 | -1.2762 | 0.020635 | 0.013714 | 0 | 0 | 3.8 | 723.5367 | 726.1148 | 727.7616 | 729.3437 | 730.8538 | 732.6458 | 734.5458 | 736.9405 | 739.8335 | 743.9499 | 749.8709 | 759.3013 | 774.4244 | 799.4636 | 840.2542 | 905.4843 | 1004.2048 | 1140.1327 | 1275.7371 | 1276.0841 | 1275.3774
3.9 | -5.0282 | -5.0354 | -5.0343 | -5.0307 | -5.0298 | -5.0266 | -5.0252 | -5.0199 | -5.014 | -5 | -4.9781 | -4.9353 | -4.8624 | -4.7312 | -4.5081 | -4.1294 | -3.5181 | -2.5793 | -1.2845 | 0.012048 | 0 | 0 | 3.9 | 723.5367 | 726.0369 | 727.5745 | 729.0047 | 730.6465 | 732.2696 | 734.1533 | 736.1153 | 738.5469 | 741.4568 | 745.5734 | 751.4772 | 760.869 | 775.9246 | 800.8605 | 841.5126 | 906.593 | 1005.2 | 1141.0505 | 1276.63 | 1276.4437
4 | -5.0286 | -5.0355 | -5.0321 | -5.0317 | -5.0292 | -5.0292 | -5.0266 | -5.0256 | -5.0206 | -5.0148 | -5.0011 | -4.9793 | -4.9368 | -4.8644 | -4.7339 | -4.5117 | -4.1344 | -3.5246 | -2.5869 | -1.2928 | 0 | 0 | 4 | 723.5367 | 725.8727 | 727.2798 | 728.8788 | 730.4228 | 732.1571 | 733.8436 | 735.7673 | 737.7518 | 740.1939 | 743.104 | 747.2108 | 753.0916 | 762.4417 | 777.4283 | 802.2598 | 842.7729 | 907.703 | 1006.1961 | 1141.9687 | 1277.1632
4.1 | -5.0281 | -5.0332 | -5.0329 | -5.0306 | -5.031 | -5.0292 | -5.0296 | -5.0273 | -5.0264 | -5.0215 | -5.0158 | -5.0022 | -4.9806 | -4.9384 | -4.8664 | -4.7365 | -4.5154 | -4.1394 | -3.531 | -2.5945 | 0 | 0 | 4.1 | 723.5367 | 725.5908 | 727.1767 | 728.6991 | 730.3907 | 731.9985 | 733.7736 | 735.4844 | 737.4217 | 739.4122 | 741.8547 | 744.7592 | 748.8529 | 754.709 | 764.0165 | 778.9335 | 803.6606 | 844.0346 | 908.8141 | 1007.1927 | 1142.3542
4.2 | -5.0254 | -5.0328 | -5.0317 | -5.0322 | -5.0306 | -5.0314 | -5.0299 | -5.0304 | -5.0282 | -5.0273 | -5.0225 | -5.0169 | -5.0033 | -4.9819 | -4.9399 | -4.8683 | -4.7392 | -4.519 | -4.1444 | -2.8848 | 0 | 0 | 4.2 | 723.5367 | 725.6026 | 727.0101 | 728.6897 | 730.2757 | 732.0082 | 733.6405 | 735.4301 | 737.1487 | 739.0896 | 741.0803 | 743.5199 | 746.4171 | 750.4968 | 756.3276 | 765.5923 | 780.44 | 805.0627 | 845.2976 | 842.0148 | 939.8925
4.3 | -5.0239 | -5.0301 | -5.0322 | -5.0317 | -5.0326 | -5.0313 | -5.0322 | -5.0307 | -5.0313 | -5.0291 | -5.0283 | -5.0235 | -5.0179 | -5.0045 | -4.9831 | -4.9415 | -4.8702 | -4.7418 | -3.871 | -2.5219 | 0 | 0 | 4.3 | 723.5367 | 725.6018 | 727.1151 | 728.5873 | 730.3076 | 731.9183 | 733.6655 | 735.3061 | 737.1003 | 738.8208 | 740.762 | 742.7511 | 745.1868 | 748.076 | 752.1414 | 757.947 | 767.169 | 781.9475 | 738.5811 | 677.1385 | 740.9783
4.4 | -5.0218 | -5.0301 | -5.0301 | -5.0326 | -5.0323 | -5.0334 | -5.0321 | -5.0331 | -5.0317 | -5.0323 | -5.0301 | -5.0293 | -5.0245 | -5.019 | -5.0056 | -4.9844 | -4.943 | -4.2216 | -3.1192 | -1.9425 | 0 | 0 | 4.4 | 723.5367 | 725.758 | 727.1782 | 728.7332 | 730.2302 | 731.9652 | 733.5842 | 735.3362 | 736.9793 | 738.7748 | 740.4954 | 742.4359 | 744.4228 | 746.8543 | 749.7354 | 753.7866 | 759.567 | 700.9269 | 614.1384 | 538.5352 | 577.9489
4.5 | -5.0215 | -5.0283 | -5.0305 | -5.0307 | -5.0333 | -5.0332 | -5.0343 | -5.033 | -5.034 | -5.0326 | -5.0332 | -5.0311 | -5.0303 | -5.0255 | -5.02 | -5.0067 | -4.336 | -3.3215 | -2.2947 | -1.3827 | 0 | 0 | 4.5 | 723.5367 | 725.7896 | 727.3748 | 728.8209 | 730.3908 | 731.8963 | 733.6362 | 735.2578 | 737.0114 | 738.6551 | 740.4508 | 742.171 | 744.1105 | 746.095 | 748.5222 | 751.3953 | 687.6979 | 592.0394 | 501.2505 | 433.8832 | 457.2537
4.6 | -5.0206 | -5.0293 | -5.0289 | -5.0312 | -5.0316 | -5.0342 | -5.0341 | -5.0352 | -5.034 | -5.035 | -5.0336 | -5.0342 | -5.032 | -5.0312 | -5.0266 | -4.3724 | -3.387 | -2.4115 | -1.5877 | -0.93418 | 0 | 0 | 4.6 | 723.5367 | 725.9235 | 727.4306 | 729.0319 | 730.4867 | 732.0617 | 733.5699 | 735.3115 | 736.9339 | 738.688 | 740.3317 | 742.1274 | 743.847 | 745.7854 | 747.7675 | 682.5484 | 584.1066 | 488.3499 | 412.1647 | 359.9578 | 373.6871
4.7 | -5.0213 | -5.0284 | -5.0301 | -5.0298 | -5.0321 | -5.0325 | -5.0352 | -5.035 | -5.0361 | -5.0349 | -5.0359 | -5.0345 | -5.0351 | -5.033 | -4.3844 | -3.4088 | -2.4506 | -1.6563 | -1.0534 | -0.60805 | 0 | 0 | 4.7 | 723.5367 | 725.917 | 727.5787 | 729.0956 | 730.7022 | 732.16 | 733.7369 | 735.2461 | 736.9883 | 738.6109 | 740.3652 | 742.0089 | 743.8044 | 745.5233 | 679.913 | 580.7006 | 483.5109 | 404.5925 | 347.3498 | 310.3868 | 318.2565
4.8 | -5.0211 | -5.03 | -5.0292 | -5.0309 | -5.0307 | -5.0331 | -5.0334 | -5.0361 | -5.036 | -5.0371 | -5.0359 | -5.0369 | -5.0355 | -4.3892 | -3.4172 | -2.4655 | -1.6814 | -1.0951 | -0.67822 | -0.38648 | 0 | 0 | 4.8 | 723.5367 | 726.0132 | 727.5802 | 729.2482 | 730.7681 | 732.3768 | 733.8357 | 735.4136 | 736.9232 | 738.6656 | 740.2883 | 742.0427 | 743.6863 | 678.029 | 578.6724 | 481.1794 | 401.5408 | 342.795 | 302.9933 | 278.0373 | 282.7107
4.9 | -5.0223 | -5.0295 | -5.0309 | -5.0301 | -5.0319 | -5.0316 | -5.034 | -5.0344 | -5.037 | -5.0369 | -5.038 | -5.0368 | -4.3918 | -3.4217 | -2.4731 | -1.6931 | -1.1126 | -0.7049 | -0.42899 | -0.24144 | 0 | 0 | 4.9 | 723.5367 | 725.9774 | 727.681 | 729.2521 | 730.922 | 732.4431 | 734.0528 | 735.5124 | 737.0908 | 738.6007 | 740.3433 | 741.966 | 676.3631 | 577.0494 | 479.5969 | 399.8643 | 340.7454 | 300.1166 | 273.5759 | 257.5927 | 260.2817
5 | -5.0225 | -5.0314 | -5.0304 | -5.0318 | -5.0311 | -5.0328 | -5.0326 | -5.0349 | -5.0353 | -5.0379 | -5.0378 | -4.3938 | -3.4251 | -2.4786 | -1.701 | -1.123 | -0.71834 | -0.44738 | -0.26852 | -0.15051 | 0 | 0 | 5 | 723.5367 | 726.0518 | 727.6477 | 729.3543 | 730.9264 | 732.5972 | 734.119 | 735.7294 | 737.1896 | 738.7684 | 740.2785 | 674.7589 | 575.5424 | 478.2316 | 398.5921 | 339.4442 | 298.6147 | 271.6187 | 254.7601 | 244.6268 | 246.3854
5.1 | -5.0239 | -5.0311 | -5.0323 | -5.0313 | -5.0327 | -5.032 | -5.0337 | -5.0335 | -5.0358 | -5.0362 | -4.3947 | -3.4282 | -2.4835 | -1.7077 | -1.1312 | -0.72788 | -0.45857 | -0.28236 | -0.16908 | -0.093963 | 0 | 0 | 5.1 | 723.5367 | 726.0019 | 727.7236 | 729.3217 | 731.029 | 732.6016 | 734.273 | 735.7953 | 737.4064 | 738.867 | 673.2788 | 574.0679 | 476.9276 | 397.4357 | 338.3599 | 297.5171 | 270.4098 | 253.3019 | 242.6888 | 236.6132 | 237.6815
5.2 | -5.0242 | -5.0331 | -5.032 | -5.0332 | -5.0323 | -5.0336 | -5.0329 | -5.0347 | -5.0344 | -4.3935 | -3.4286 | -2.4873 | -1.7142 | -1.1388 | -0.73629 | -0.46767 | -0.29231 | -0.18045 | -0.10788 | -0.060452 | 0 | 0 | 5.2 | 723.5367 | 726.0665 | 727.6745 | 729.3981 | 730.9966 | 732.7044 | 734.2772 | 735.9492 | 737.4718 | 672.011 | 572.8688 | 475.7473 | 396.3113 | 337.3369 | 296.5353 | 269.418 | 252.2482 | 241.4992 | 235.1631 | 231.395 | 232.2624
5.3 | -5.0256 | -5.0328 | -5.034 | -5.0329 | -5.0341 | -5.0332 | -5.0346 | -5.0339 | -4.3932 | -3.4288 | -2.489 | -1.7179 | -1.1452 | -0.74438 | -0.47616 | -0.30115 | -0.18973 | -0.11791 | -0.071851 | -0.039989 | 0 | 0 | 5.3 | 723.5367 | 726.0112 | 727.7396 | 729.3492 | 731.0732 | 732.6719 | 734.38 | 735.9532 | 670.6478 | 571.6855 | 474.7785 | 395.4618 | 336.4374 | 295.5857 | 268.4877 | 251.3105 | 240.5269 | 234.1175 | 230.2087 | 228.1041 | 228.6859
5.4 | -5.026 | -5.0349 | -5.0338 | -5.0349 | -5.0339 | -5.0351 | -5.0341 | -4.3941 | -3.4303 | -2.4916 | -1.7216 | -1.1496 | -0.74982 | -0.48346 | -0.30966 | -0.1984 | -0.12682 | -0.081158 | -0.050028 | -0.028601 | 0 | 0 | 5.4 | 723.5367 | 726.0718 | 727.6846 | 729.4146 | 731.0244 | 732.7486 | 734.3474 | 669.1727 | 570.3785 | 473.7139 | 394.6274 | 335.749 | 294.9107 | 267.6811 | 250.4054 | 239.6163 | 233.1881 | 229.2398 | 227.0599 | 225.7119 | 226.3161
5.5 | -5.0275 | -5.0347 | -5.0358 | -5.0347 | -5.0358 | -5.0348 | -4.3955 | -3.4326 | -2.4952 | -1.7264 | -1.1549 | -0.75511 | -0.48872 | -0.31552 | -0.20589 | -0.13541 | -0.089869 | -0.058948 | -0.037913 | -0.021436 | 0 | 0 | 5.5 | 723.5367 | 726.0147 | 727.7455 | 729.3597 | 731.09 | 732.6998 | 667.6355 | 568.9844 | 472.5373 | 393.6691 | 334.9644 | 294.2507 | 267.0856 | 249.7749 | 238.8295 | 232.2913 | 228.3326 | 226.1318 | 224.7436 | 224.0871 | 224.5271
5.6 | -5.0278 | -5.0367 | -5.0356 | -5.0367 | -5.0356 | -4.3971 | -3.4353 | -2.4995 | -1.732 | -1.1612 | -0.76159 | -0.4949 | -0.32124 | -0.21134 | -0.14136 | -0.097386 | -0.067553 | -0.046629 | -0.030359 | -0.017915 | 0 | 0 | 5.6 | 723.5367 | 726.0736 | 727.6886 | 729.4208 | 731.0351 | 666.0711 | 567.5484 | 471.2984 | 392.6236 | 334.0678 | 293.4668 | 266.3941 | 249.1596 | 238.254 | 231.6694 | 227.5494 | 225.2365 | 223.837 | 223.1593 | 222.6643 | 223.1927
5.7 | -5.0293 | -5.0365 | -5.0376 | -5.0365 | -4.3989 | -3.4381 | -2.504 | -1.738 | -1.1682 | -0.76889 | -0.50215 | -0.32815 | -0.21771 | -0.14715 | -0.10287 | -0.073512 | -0.054152 | -0.038965 | -0.026632 | -0.015339 | 0 | 0 | 5.7 | 723.5367 | 726.0162 | 727.7476 | 729.3639 | 664.4961 | 566.0952 | 470.0321 | 391.5359 | 333.109 | 292.5959 | 265.5907 | 248.4205 | 237.5826 | 231.0626 | 226.9775 | 224.616 | 223.0544 | 222.2643 | 221.7579 | 221.5977 | 221.9972
5.8 | -5.0296 | -5.0385 | -5.0374 | -4.4007 | -3.441 | -2.5086 | -1.7442 | -1.1754 | -0.77659 | -0.50999 | -0.33588 | -0.22515 | -0.15414 | -0.10928 | -0.079325 | -0.059642 | -0.044927 | -0.034156 | -0.023947 | -0.014466 | 0 | 0 | 5.8 | 723.5367 | 726.0743 | 727.6904 | 662.917 | 564.6354 | 468.755 | 390.4309 | 332.1228 | 291.6829 | 264.7253 | 247.5947 | 236.7995 | 230.3323 | 226.3097 | 224.0108 | 222.4832 | 221.6441 | 220.9755 | 220.7027 | 220.493 | 221
5.9 | -5.0311 | -5.0383 | -4.4025 | -3.444 | -2.5133 | -1.7504 | -1.1827 | -0.78445 | -0.51808 | -0.34401 | -0.23319 | -0.16196 | -0.11675 | -0.086325 | -0.066053 | -0.050743 | -0.039647 | -0.029909 | -0.021991 | -0.013402 | 0 | 0 | 5.9 | 723.5367 | 726.0171 | 661.3364 | 563.1731 | 467.4737 | 389.3191 | 331.1257 | 290.7527 | 263.8328 | 246.7271 | 235.9546 | 229.5153 | 225.5303 | 223.2821 | 221.816 | 221.0392 | 220.4043 | 220.0827 | 219.7106 | 219.6064 | 219.9944
6 | -5.0314 | -4.4043 | -3.4469 | -2.5179 | -1.7567 | -1.19 | -0.79236 | -0.52627 | -0.3523 | -0.24147 | -0.17017 | -0.12482 | -0.094156 | -0.073536 | -0.057745 | -0.04606 | -0.035725 | -0.027482 | -0.019365 | -0.01236 | 0 | 0 | 6 | 723.5367 | 659.7563 | 561.7096 | 466.1906 | 388.2046 | 330.1244 | 289.8159 | 262.9296 | 245.8425 | 235.0827 | 228.6567 | 224.6893 | 222.4667 | 221.0375 | 220.3108 | 219.7374 | 219.4779 | 219.1395 | 218.9864 | 218.7093 | 219.1037
6.1 | -4.3977 | -3.4498 | -2.5225 | -1.7629 | -1.1973 | -0.80028 | -0.53448 | -0.36064 | -0.24986 | -0.17854 | -0.13315 | -0.10239 | -0.081611 | -0.06558 | -0.053544 | -0.042728 | -0.033895 | -0.025181 | -0.017852 | -0.010246 | 0 | 0 | 6.1 | 723.5367 | 560.2467 | 464.9065 | 387.0887 | 329.1213 | 288.8764 | 262.0224 | 244.9515 | 234.2005 | 227.7813 | 223.8214 | 221.6099 | 220.1972 | 219.4958 | 218.959 | 218.7496 | 218.4727 | 218.3816 | 218.1382 | 218.0383 | 218.2639
6.2 | -3.1292 | -2.2087 | -1.7692 | -1.2046 | -0.8082 | -0.54271 | -0.369 | -0.25828 | -0.18698 | -0.14157 | -0.11078 | -0.089943 | -0.073812 | -0.061621 | -0.050563 | -0.04138 | -0.032185 | -0.024265 | -0.016062 | -0.0095301 | 0 | 0 | 6.2 | 723.5367 | 496.7353 | 385.972 | 328.1172 | 287.9357 | 261.1137 | 244.0581 | 233.3145 | 226.8996 | 222.9433 | 220.7363 | 219.3302 | 218.6394 | 218.119 | 217.9347 | 217.6943 | 217.6534 | 217.4714 | 217.4335 | 217.273 | 217.6184
6.3 | -1.5739 | -0.82202 | -0.89392 | -0.81613 | -0.55093 | -0.37737 | -0.2667 | -0.19543 | -0.15002 | -0.11922 | -0.098372 | -0.082205 | -0.069954 | -0.058797 | -0.049457 | -0.04002 | -0.03175 | -0.023066 | -0.015943 | -0.0089201 | 0 | 0 | 6.3 | 723.5367 | 484.0521 | 360.2248 | 286.9944 | 260.2042 | 243.1638 | 232.4271 | 226.0157 | 222.0614 | 219.8564 | 218.4529 | 217.7662 | 217.2522 | 217.0784 | 216.8544 | 216.8386 | 216.6931 | 216.7053 | 216.6062 | 216.6909 | 216.9502
6.4 | -0.045382 | 0.51417 | 0.12894 | -0.24112 | -0.38573 | -0.27513 | -0.20388 | -0.15849 | -0.12769 | -0.10683 | -0.090656 | -0.078384 | -0.06719 | -0.05779 | -0.048254 | -0.039826 | -0.030901 | -0.023428 | -0.015924 | -0.0096262 | 0 | 0 | 6.4 | 723.5367 | 506.5299 | 385.2166 | 292.3832 | 242.269 | 231.5392 | 225.131 | 221.1783 | 218.9745 | 217.5719 | 216.8868 | 216.3751 | 216.2053 | 215.9877 | 215.9823 | 215.8532 | 215.8905 | 215.8279 | 215.9627 | 215.9493 | 216.3568
6.5 | 1.2779 | 1.6687 | 1.1663 | 0.55906 | 0.034504 | -0.21233 | -0.16696 | -0.13616 | -0.11531 | -0.099127 | -0.086849 | -0.075642 | -0.066221 | -0.056648 | -0.04816 | -0.039135 | -0.031505 | -0.023759 | -0.017111 | -0.0098572 | 0 | 0 | 6.5 | 723.5367 | 545.3139 | 438.7221 | 340.4996 | 263.7294 | 224.246 | 220.2948 | 218.0918 | 216.6898 | 216.0054 | 215.4945 | 215.3261 | 215.1107 | 215.1093 | 214.9865 | 215.0343 | 214.988 | 215.1479 | 215.1711 | 215.3319 | 215.6527
6.6 | 2.329 | 2.5908 | 2.0979 | 1.4415 | 0.73232 | 0.14265 | -0.14463 | -0.12378 | -0.1076 | -0.095324 | -0.084114 | -0.074686 | -0.0651 | -0.056591 | -0.047529 | -0.039839 | -0.031993 | -0.025188 | -0.017693 | -0.010871 | 0 | 0 | 6.6 | 723.5367 | 586.9315 | 500.5945 | 410.063 | 322.4757 | 252.4855 | 217.2089 | 215.8072 | 215.1232 | 214.6126 | 214.4449 | 214.2302 | 214.2302 | 214.1097 | 214.1614 | 214.1214 | 214.2918 | 214.3312 | 214.5172 | 214.5223 | 214.9798
6.7 | 3.1132 | 3.2826 | 2.864 | 2.2702 | 1.5492 | 0.7999 | 0.18581 | -0.11608 | -0.1038 | -0.092591 | -0.083162 | -0.073571 | -0.065057 | -0.055981 | -0.04827 | -0.040387 | -0.033522 | -0.025926 | -0.018948 | -0.011071 | 0 | 0 | 6.7 | 723.5367 | 624.0817 | 558.2469 | 482.5264 | 398.7975 | 315.4333 | 247.9978 | 214.2408 | 213.7303 | 213.5629 | 213.3485 | 213.3491 | 213.2292 | 213.2824 | 213.2446 | 213.4189 | 213.4647 | 213.6611 | 213.6825 | 213.8287 | 214.1859
6.8 | 3.67 | 3.7781 | 3.4523 | 2.9702 | 2.3368 | 1.5919 | 0.82834 | 0.20578 | -0.10107 | -0.09164 | -0.082048 | -0.073533 | -0.064453 | -0.056735 | -0.048839 | -0.041953 | -0.034321 | -0.027282 | -0.019305 | -0.011895 | 0 | 0 | 6.8 | 723.5367 | 653.8439 | 605.9374 | 546.877 | 475.4151 | 394.2771 | 312.4567 | 245.9204 | 212.6807 | 212.4664 | 212.4672 | 212.3476 | 212.4013 | 212.3642 | 212.5399 | 212.5879 | 212.7882 | 212.8159 | 212.9726 | 212.9491 | 213.4318
6.9 | 4.0509 | 4.1191 | 3.8816 | 3.517 | 3.0115 | 2.3644 | 1.6115 | 0.84324 | 0.21794 | -0.090527 | -0.082011 | -0.07293 | -0.065211 | -0.057311 | -0.050418 | -0.042773 | -0.035713 | -0.027699 | -0.020229 | -0.01186 | 0 | 0 | 6.9 | 723.5367 | 676.0544 | 642.3604 | 598.6682 | 542.2293 | 472.358 | 392.1621 | 310.8865 | 244.6558 | 211.5852 | 211.4656 | 211.5195 | 211.4827 | 211.6589 | 211.7076 | 211.9093 | 211.9392 | 212.0998 | 212.0826 | 212.1986 | 212.5721
7 | 4.3033 | 4.3472 | 4.1814 | 3.9208 | 3.5427 | 3.0297 | 2.3784 | 1.6233 | 0.85367 | 0.22756 | -0.081409 | -0.07369 | -0.065788 | -0.058894 | -0.051245 | -0.044179 | -0.036151 | -0.02866 | -0.020254 | -0.012468 | 0 | 0 | 7 | 723.5367 | 691.7481 | 668.6604 | 637.5298 | 595.4361 | 539.9776 | 470.7025 | 390.8579 | 309.7802 | 243.6543 | 210.6375 | 210.6007 | 210.7772 | 210.8261 | 211.0283 | 211.0589 | 211.2208 | 211.2059 | 211.3257 | 211.2757 | 211.7687
7.1 | 4.4669 | 4.4954 | 4.3845 | 4.2052 | 3.937 | 3.5549 | 3.04 | 2.388 | 1.6325 | 0.86267 | 0.23587 | -0.074267 | -0.067373 | -0.059722 | -0.052654 | -0.044623 | -0.037125 | -0.028707 | -0.020899 | -0.012257 | 0 | 0 | 7.1 | 723.5367 | 702.4367 | 686.8032 | 665.2511 | 635.0838 | 593.5989 | 538.5327 | 469.5089 | 389.8158 | 308.8214 | 242.7886 | 209.8953 | 209.9442 | 210.1466 | 210.1774 | 210.3399 | 210.3256 | 210.4469 | 210.399 | 210.4942 | 210.874
7.2 | 4.5706 | 4.5906 | 4.5178 | 4.399 | 4.2155 | 3.9454 | 3.5627 | 3.0478 | 2.3961 | 1.6404 | 0.8697 | 0.24218 | -0.0682 | -0.061133 | -0.0531 | -0.045601 | -0.037178 | -0.029365 | -0.02071 | -0.012734 | 0 | 0 | 7.2 | 723.5367 | 709.4554 | 698.9345 | 684.2059 | 663.2298 | 633.4405 | 592.2211 | 537.3484 | 468.4618 | 388.9089 | 308.0677 | 242.1312 | 209.2648 | 209.2956 | 209.4583 | 209.4442 | 209.5659 | 209.5188 | 209.6154 | 209.55 | 210.0469
7.3 | 4.6357 | 4.6501 | 4.6041 | 4.5269 | 4.4059 | 4.2214 | 3.9513 | 3.569 | 3.0543 | 2.4023 | 1.6463 | 0.87565 | 0.24841 | -0.061578 | -0.05408 | -0.045656 | -0.037841 | -0.029181 | -0.021199 | -0.01243 | 0 | 0 | 7.3 | 723.5367 | 713.9819 | 706.7887 | 696.7952 | 682.4072 | 661.6653 | 632.0563 | 590.9888 | 536.2984 | 467.6191 | 388.2099 | 307.4256 | 241.4818 | 208.5765 | 208.5625 | 208.6844 | 208.6374 | 208.7345 | 208.6698 | 208.7545 | 209.1365
7.4 | 4.676 | 4.6877 | 4.6585 | 4.6101 | 4.5316 | 4.4102 | 4.2259 | 3.9558 | 3.5734 | 3.0588 | 2.4073 | 1.6521 | 0.88216 | 0.25545 | -0.054134 | -0.046319 | -0.037659 | -0.029675 | -0.020902 | -0.012844 | 0 | 0 | 7.4 | 723.5367 | 716.8064 | 711.7941 | 704.9042 | 695.1107 | 680.8662 | 660.2456 | 630.8057 | 589.9601 | 535.4555 | 466.8874 | 387.5184 | 306.7254 | 240.7476 | 207.8027 | 207.7557 | 207.853 | 207.7884 | 207.8736 | 207.801 | 208.2993
7.5 | 4.701 | 4.7107 | 4.6932 | 4.6627 | 4.6135 | 4.5349 | 4.4132 | 4.2285 | 3.9584 | 3.5766 | 3.0633 | 2.413 | 1.6587 | 0.88948 | 0.2632 | -0.046137 | -0.038154 | -0.029379 | -0.02132 | -0.012498 | 0 | 0 | 7.5 | 723.5367 | 718.5707 | 714.8895 | 710.0503 | 703.2762 | 693.5702 | 679.4586 | 659.0293 | 629.7619 | 589.0419 | 534.6196 | 466.0973 | 386.742 | 305.9396 | 239.9399 | 206.9713 | 206.9068 | 206.9921 | 206.9197 | 206.9998 | 207.3824
7.6 | 4.7165 | 4.7255 | 4.7145 | 4.6962 | 4.6654 | 4.6157 | 4.5363 | 4.4142 | 4.2299 | 3.9608 | 3.5804 | 3.0685 | 2.4194 | 1.6661 | 0.89736 | 0.27135 | -0.037857 | -0.029798 | -0.020975 | -0.012885 | 0 | 0 | 7.6 | 723.5367 | 719.6232 | 716.8062 | 713.2223 | 708.4499 | 701.7814 | 692.2329 | 678.2576 | 657.9232 | 628.7247 | 588.065 | 533.6984 | 465.221 | 385.8916 | 305.0961 | 239.0899 | 206.1105 | 206.0381 | 206.1184 | 206.0427 | 206.5414
7.7 | 4.7264 | 4.7345 | 4.7283 | 4.7169 | 4.698 | 4.6661 | 4.6159 | 4.5366 | 4.4152 | 4.2319 | 3.9641 | 3.5851 | 3.0744 | 2.4264 | 1.6738 | 0.90551 | 0.2797 | -0.029453 | -0.021364 | -0.012522 | 0 | 0 | 7.7 | 723.5367 | 720.2751 | 717.9433 | 715.1806 | 711.6877 | 707.0526 | 700.4929 | 691.0058 | 677.0633 | 656.7585 | 627.6023 | 587.0018 | 532.7029 | 464.2867 | 384.9988 | 304.2229 | 238.2201 | 205.2368 | 205.1611 | 205.2395 | 205.6222
7.8 | 4.7327 | 4.7409 | 4.7368 | 4.7299 | 4.7174 | 4.6978 | 4.6658 | 4.616 | 4.5374 | 4.4169 | 4.2347 | 3.9681 | 3.5902 | 3.0807 | 2.4337 | 1.6817 | 0.91379 | 0.28812 | -0.021 | -0.012899 | 0 | 0 | 7.8 | 723.5367 | 720.6416 | 718.642 | 716.3928 | 713.7576 | 710.3593 | 705.7651 | 699.2112 | 689.7202 | 675.7841 | 655.5078 | 626.4057 | 585.8803 | 531.6644 | 463.3223 | 384.0857 | 303.3366 | 237.342 | 204.3579 | 204.281 | 204.7799
7.9 | 4.7373 | 4.7449 | 4.7424 | 4.7372 | 4.7295 | 4.7169 | 4.6975 | 4.6661 | 4.6169 | 4.539 | 4.4194 | 4.2381 | 3.9724 | 3.5957 | 3.0872 | 2.441 | 1.6897 | 0.92212 | 0.29657 | -0.012529 | 0 | 0 | 7.9 | 723.5367 | 720.8768 | 719.0869 | 717.209 | 715.048 | 712.4441 | 709.0374 | 704.4194 | 697.8448 | 688.3492 | 674.431 | 654.1991 | 625.1661 | 584.7284 | 530.6053 | 462.3442 | 383.1639 | 302.445 | 236.4607 | 203.4771 | 203.8598
8 | 4.7404 | 4.7478 | 4.7452 | 4.7419 | 4.7366 | 4.7291 | 4.7169 | 4.698 | 4.6671 | 4.6185 | 4.5412 | 4.4222 | 4.2417 | 3.977 | 3.6012 | 3.0938 | 2.4485 | 1.6977 | 0.93046 | 0.30503 | 0 | 0 | 8 | 723.5367 | 721.0464 | 719.4415 | 717.7358 | 715.8851 | 713.7095 | 711.0725 | 707.6312 | 702.9887 | 696.4052 | 686.9206 | 673.0355 | 652.8602 | 623.9058 | 583.5625 | 529.5369 | 461.3602 | 382.2385 | 301.5512 | 235.5782 | 203.0171
8.1 | 4.7426 | 4.749 | 4.7473 | 4.7445 | 4.7414 | 4.7365 | 4.7295 | 4.7177 | 4.6992 | 4.6687 | 4.6205 | 4.5437 | 4.4252 | 4.2454 | 3.9816 | 3.6068 | 3.1003 | 2.4559 | 1.7058 | 0.9388 | 0 | 0 | 8.1 | 723.5367 | 721.2388 | 719.6941 | 718.1135 | 716.3907 | 714.5031 | 712.2869 | 709.6161 | 706.1521 | 701.5007 | 694.9234 | 685.4622 | 671.6194 | 651.5074 | 622.636 | 582.3903 | 528.4643 | 460.3736 | 381.3115 | 300.6566 | 235.1555
8.2 | 4.7434 | 4.7499 | 4.7483 | 4.7468 | 4.7444 | 4.7418 | 4.7372 | 4.7305 | 4.719 | 4.7008 | 4.6706 | 4.6227 | 4.5462 | 4.4283 | 4.2492 | 3.9862 | 3.6124 | 3.1069 | 2.4633 | 1.5548 | 0 | 0 | 8.2 | 723.5367 | 721.3706 | 719.9103 | 718.3462 | 716.7273 | 714.9616 | 713.0365 | 710.7917 | 708.1028 | 704.6312 | 699.9833 | 693.4215 | 683.9902 | 670.1941 | 650.1483 | 621.362 | 581.2151 | 527.3896 | 459.3855 | 396.9115 | 316.7123
8.3 | 4.7436 | 4.7498 | 4.7494 | 4.7482 | 4.747 | 4.7451 | 4.7428 | 4.7384 | 4.732 | 4.7207 | 4.7026 | 4.6726 | 4.6249 | 4.5489 | 4.4314 | 4.253 | 3.9908 | 3.618 | 2.9547 | 1.9159 | 0 | 0 | 8.3 | 723.5367 | 721.4663 | 720.0226 | 718.5222 | 716.9146 | 715.2567 | 713.4602 | 711.5133 | 709.2549 | 706.5603 | 703.0903 | 698.4525 | 691.9107 | 682.5123 | 668.7648 | 648.7863 | 620.0857 | 580.0381 | 542.8399 | 516.1118 | 437.6446
8.4 | 4.7431 | 4.7499 | 4.7496 | 4.7496 | 4.7488 | 4.748 | 4.7463 | 4.7441 | 4.74 | 4.7336 | 4.7224 | 4.7045 | 4.6746 | 4.6272 | 4.5515 | 4.4346 | 4.2567 | 3.8368 | 3.0694 | 1.9806 | 0 | 0 | 8.4 | 723.5367 | 721.4771 | 720.0784 | 718.5897 | 717.05 | 715.4108 | 713.7298 | 711.9174 | 709.961 | 707.6983 | 705.0046 | 701.5407 | 696.9161 | 690.3961 | 681.0316 | 667.3335 | 647.4226 | 635.3261 | 636.5611 | 643.851 | 576.4834
8.5 | 4.7429 | 4.7495 | 4.7501 | 4.7503 | 4.7506 | 4.75 | 4.7494 | 4.7478 | 4.7457 | 4.7416 | 4.7353 | 4.7242 | 4.7064 | 4.6767 | 4.6295 | 4.5541 | 4.2793 | 3.707 | 2.8621 | 1.8208 | 0 | 0 | 8.5 | 723.5367 | 721.4702 | 720.0448 | 718.6055 | 717.085 | 715.5217 | 713.8657 | 712.1739 | 710.3549 | 708.3957 | 706.1332 | 703.4433 | 699.9875 | 695.3771 | 688.8796 | 679.5496 | 682.404 | 703.721 | 736.089 | 766.091 | 713.1344
8.6 | 4.7426 | 4.7498 | 4.7501 | 4.7511 | 4.7514 | 4.752 | 4.7515 | 4.7509 | 4.7494 | 4.7474 | 4.7433 | 4.7371 | 4.726 | 4.7083 | 4.6787 | 4.4736 | 4.004 | 3.3046 | 2.4589 | 1.539 | 0 | 0 | 8.6 | 723.5367 | 721.4151 | 719.9982 | 718.5397 | 717.0767 | 715.5391 | 713.9645 | 712.3011 | 710.6051 | 708.784 | 706.8249 | 704.5645 | 701.8797 | 698.4327 | 693.8369 | 703.8459 | 735.6719 | 782.9216 | 832.9686 | 873.4076 | 834.2698
8.7 | 4.7429 | 4.7499 | 4.7507 | 4.7513 | 4.7524 | 4.7529 | 4.7535 | 4.753 | 4.7525 | 4.751 | 4.749 | 4.745 | 4.7388 | 4.7278 | 4.5523 | 4.1288 | 3.4996 | 2.7569 | 1.9827 | 1.2214 | 0 | 0 | 8.7 | 723.5367 | 721.3776 | 719.9112 | 718.4694 | 716.9937 | 715.5192 | 713.9738 | 712.3944 | 710.7281 | 709.0308 | 707.2095 | 705.2517 | 702.9942 | 700.3149 | 713.3392 | 749.8326 | 804.1573 | 864.6481 | 919.955 | 961.4495 | 933.8477
8.8 | 4.7433 | 4.7508 | 4.7511 | 4.7521 | 4.7528 | 4.7539 | 4.7545 | 4.7551 | 4.7547 | 4.7542 | 4.7527 | 4.7507 | 4.7467 | 4.5829 | 4.1784 | 3.5793 | 2.8834 | 2.1794 | 1.5209 | 0.92336 | 0 | 0 | 8.8 | 723.5367 | 721.3174 | 719.8502 | 718.3656 | 716.9121 | 715.4284 | 713.9487 | 712.4 | 710.8188 | 709.1515 | 707.4542 | 705.6334 | 703.6775 | 717.8629 | 756.2123 | 813.4753 | 878.5619 | 940.9158 | 992.8793 | 1029.9771 | 1011.1443
8.9 | 4.7442 | 4.7514 | 4.7521 | 4.7525 | 4.7536 | 4.7543 | 4.7555 | 4.7561 | 4.7567 | 4.7563 | 4.7558 | 4.7543 | 4.5949 | 4.1979 | 3.6112 | 2.9348 | 2.2613 | 1.6492 | 1.1214 | 0.67193 | 0 | 0 | 8.9 | 723.5367 | 721.2893 | 719.7732 | 718.2933 | 716.8006 | 715.3419 | 713.8547 | 712.3729 | 710.8228 | 709.2411 | 707.5735 | 705.8765 | 720.4736 | 759.4897 | 817.8398 | 884.7118 | 949.9722 | 1006.5508 | 1050.7472 | 1081.0808 | 1068.5642
9 | 4.7451 | 4.7527 | 4.7528 | 4.7536 | 4.7541 | 4.7552 | 4.7559 | 4.7571 | 4.7577 | 4.7583 | 4.7579 | 4.6002 | 4.2062 | 3.6246 | 2.9563 | 2.2954 | 1.7027 | 1.2048 | 0.80123 | 0.47467 | 0 | 0 | 9 | 723.5367 | 721.2448 | 719.7338 | 718.2087 | 716.7236 | 715.2274 | 713.7664 | 712.2775 | 710.7949 | 709.2441 | 707.6622 | 722.3887 | 761.6087 | 820.2984 | 887.7676 | 954.0836 | 1012.4649 | 1059.6175 | 1094.623 | 1117.9571 | 1109.7548
9.1 | 4.7464 | 4.7537 | 4.7542 | 4.7544 | 4.7552 | 4.7557 | 4.7568 | 4.7575 | 4.7588 | 4.7593 | 4.6029 | 4.2106 | 3.6313 | 2.9667 | 2.3111 | 1.7264 | 1.2406 | 0.85582 | 0.55871 | 0.32765 | 0 | 0 | 9.1 | 723.5367 | 721.2333 | 719.6817 | 718.1646 | 716.6359 | 715.1486 | 713.6507 | 712.1887 | 710.6989 | 709.2158 | 724.0358 | 763.3165 | 822.0643 | 889.6687 | 956.293 | 1015.2886 | 1063.5454 | 1100.41 | 1126.7477 | 1143.8428 | 1138.5328
9.2 | 4.7476 | 4.7553 | 4.7553 | 4.7558 | 4.756 | 4.7568 | 4.7573 | 4.7584 | 4.7592 | 4.6036 | 4.2127 | 3.6354 | 2.9731 | 2.3202 | 1.7389 | 1.2581 | 0.88066 | 0.59518 | 0.38263 | 0.22259 | 0 | 0 | 9.2 | 723.5367 | 721.2036 | 719.6654 | 718.1093 | 716.5901 | 715.0598 | 713.5714 | 712.0725 | 710.6098 | 725.4676 | 764.793 | 823.5632 | 891.1599 | 957.8113 | 1016.9593 | 1065.5728 | 1103.1076 | 1130.5971 | 1149.5847 | 1161.6863 | 1158.2218
9.3 | 4.7492 | 4.7565 | 4.7569 | 4.7569 | 4.7574 | 4.7576 | 4.7584 | 4.7589 | 4.6034 | 4.2133 | 3.6375 | 2.9772 | 2.3267 | 1.7475 | 1.2688 | 0.89438 | 0.61334 | 0.40786 | 0.25926 | 0.14973 | 0 | 0 | 9.3 | 723.5367 | 721.204 | 719.6325 | 718.0911 | 716.5335 | 715.0133 | 713.4821 | 711.9931 | 726.8188 | 766.1105 | 824.8476 | 892.4206 | 959.0634 | 1018.2208 | 1066.9097 | 1104.6526 | 1132.5462 | 1152.2376 | 1165.5117 | 1173.7951 | 1171.5259
9.4 | 4.7505 | 4.7583 | 4.7581 | 4.7585 | 4.7585 | 4.759 | 4.7592 | 4.6036 | 4.2137 | 3.6387 | 2.9799 | 2.3311 | 1.7539 | 1.277 | 0.90415 | 0.62485 | 0.422 | 0.27764 | 0.17508 | 0.10069 | 0 | 0 | 9.4 | 723.5367 | 721.1833 | 719.631 | 718.0569 | 716.5147 | 714.9562 | 713.4355 | 728.2061 | 767.4177 | 826.0518 | 893.523 | 960.1015 | 1019.2522 | 1067.9807 | 1105.7886 | 1133.8048 | 1153.7378 | 1167.437 | 1176.4359 | 1181.9972 | 1180.4449
9.5 | 4.7522 | 4.7596 | 4.7599 | 4.7597 | 4.7601 | 4.7601 | 4.6045 | 4.2148 | 3.6404 | 2.9824 | 2.3347 | 1.7587 | 1.2831 | 0.9117 | 0.63379 | 0.4322 | 0.28938 | 0.18933 | 0.11912 | 0.068251 | 0 | 0 | 9.5 | 723.5367 | 721.1902 | 719.609 | 718.0547 | 716.4798 | 714.9372 | 729.6577 | 768.7839 | 827.2924 | 894.6154 | 961.0599 | 1020.1257 | 1068.8378 | 1106.6944 | 1134.7973 | 1154.8288 | 1168.6715 | 1177.9241 | 1183.9165 | 1187.5423 | 1186.4556
9.6 | 4.7536 | 4.7613 | 4.7611 | 4.7614 | 4.7613 | 4.6058 | 4.2164 | 3.6426 | 2.9855 | 2.3386 | 1.7634 | 1.2885 | 0.91771 | 0.64067 | 0.44017 | 0.29854 | 0.19964 | 0.13091 | 0.082525 | 0.047347 | 0 | 0 | 9.6 | 723.5367 | 721.1742 | 719.6151 | 718.032 | 716.4773 | 731.1587 | 770.2094 | 828.5974 | 895.767 | 962.055 | 1020.9895 | 1069.6155 | 1107.4424 | 1135.576 | 1155.6896 | 1169.6399 | 1179.0028 | 1185.1452 | 1189.0276 | 1191.379 | 1190.5471
9.7 | 4.7553 | 4.7627 | 4.7629 | 4.7627 | 4.6073 | 4.2183 | 3.6453 | 2.9891 | 2.3432 | 1.7687 | 1.2942 | 0.92363 | 0.64677 | 0.44662 | 0.30565 | 0.20772 | 0.14013 | 0.092858 | 0.059146 | 0.033953 | 0 | 0 | 9.7 | 723.5367 | 721.1841 | 719.5984 | 718.0378 | 732.6882 | 771.6732 | 829.9518 | 896.9781 | 963.1147 | 1021.9127 | 1070.4299 | 1108.1806 | 1136.275 | 1156.3923 | 1170.3942 | 1179.8512 | 1186.1075 | 1190.1036 | 1192.6063 | 1194.0777 | 1193.4245
9.8 | 4.7567 | 4.7645 | 4.7642 | 4.609 | 4.2205 | 3.6482 | 2.9932 | 2.3483 | 1.7745 | 1.3005 | 0.93011 | 0.65322 | 0.45297 | 0.31198 | 0.21429 | 0.1473 | 0.10097 | 0.068381 | 0.044292 | 0.025637 | 0 | 0 | 9.8 | 723.5367 | 721.1702 | 719.608 | 734.2319 | 773.1575 | 831.3347 | 898.2276 | 964.2238 | 1022.8952 | 1071.3088 | 1108.9781 | 1137.0106 | 1157.0851 | 1171.0688 | 1180.5414 | 1186.8557 | 1190.949 | 1193.5673 | 1195.1529 | 1196.0903 | 1195.5162
9.9 | 4.7584 | 4.7658 | 4.6108 | 4.2227 | 3.6513 | 2.9974 | 2.3536 | 1.7807 | 1.3073 | 0.93715 | 0.66028 | 0.45988 | 0.31867 | 0.22076 | 0.15369 | 0.10757 | 0.075555 | 0.052413 | 0.034875 | 0.020398 | 0 | 0 | 9.9 | 723.5367 | 721.1814 | 735.782 | 774.6515 | 832.7319 | 899.4976 | 965.3617 | 1023.9164 | 1072.2371 | 1109.8349 | 1137.8106 | 1157.837 | 1171.7798 | 1181.2216 | 1187.5241 | 1191.6363 | 1194.3141 | 1195.9977 | 1197.0509 | 1197.6372 | 1197.1361
10 | 4.7598 | 4.6125 | 4.225 | 3.6545 | 3.0016 | 2.359 | 1.7871 | 1.3143 | 0.94454 | 0.6678 | 0.46735 | 0.32596 | 0.22779 | 0.16043 | 0.11406 | 0.081961 | 0.059012 | 0.042052 | 0.028521 | 0.017028 | 0 | 0 | 10 | 723.5367 | 737.334 | 776.1498 | 834.1357 | 900.7775 | 966.5138 | 1024.9581 | 1073.194 | 1110.73 | 1138.6597 | 1158.6479 | 1172.5549 | 1181.9608 | 1188.2288 | 1192.3134 | 1194.981 | 1196.6843 | 1197.7974 | 1198.4819 | 1198.9066 | 1198.4471
10.1 | 4.6067 | 4.2273 | 3.6576 | 3.0059 | 2.3645 | 1.7935 | 1.3215 | 0.95212 | 0.67559 | 0.47519 | 0.33372 | 0.23538 | 0.16778 | 0.12112 | 0.088714 | 0.065513 | 0.048461 | 0.035121 | 0.024205 | 0.014427 | 0 | 0 | 10.1 | 723.5367 | 777.649 | 835.5425 | 902.0619 | 967.6728 | 1026.0096 | 1074.1652 | 1111.6455 | 1139.5371 | 1159.497 | 1173.379 | 1182.7588 | 1188.9975 | 1193.0495 | 1195.6842 | 1197.3608 | 1198.464 | 1199.1683 | 1199.6529 | 1199.9472 | 1199.5621
10.2 | 4.145 | 3.5832 | 3.0103 | 2.37 | 1.8 | 1.3287 | 0.95979 | 0.68351 | 0.48321 | 0.34175 | 0.24334 | 0.1756 | 0.12874 | 0.096082 | 0.07258 | 0.055217 | 0.041624 | 0.030615 | 0.021028 | 0.012539 | 0 | 0 | 10.2 | 723.5367 | 828.8781 | 903.3485 | 968.8348 | 1027.0658 | 1075.143 | 1112.5706 | 1140.4286 | 1160.3661 | 1174.2312 | 1183.5948 | 1189.815 | 1193.8443 | 1196.4514 | 1198.0961 | 1199.1668 | 1199.8446 | 1200.3194 | 1200.6336 | 1200.8659 | 1200.5047
10.3 | 3.3485 | 2.7051 | 2.298 | 1.8065 | 1.3359 | 0.96748 | 0.69147 | 0.49131 | 0.3499 | 0.25148 | 0.18369 | 0.13673 | 0.10392 | 0.08021 | 0.062588 | 0.048691 | 0.037372 | 0.027531 | 0.018949 | 0.011134 | 0 | 0 | 10.3 | 723.5367 | 872.4369 | 961.927 | 1028.1241 | 1076.124 | 1113.5002 | 1141.3265 | 1161.2447 | 1175.0972 | 1184.4507 | 1190.6606 | 1194.677 | 1197.2673 | 1198.8901 | 1199.9336 | 1200.5797 | 1201.0221 | 1201.3098 | 1201.5324 | 1201.6624 | 1201.3372
10.4 | 2.3052 | 1.672 | 1.504 | 1.2657 | 0.97518 | 0.69946 | 0.49945 | 0.35811 | 0.25971 | 0.19191 | 0.14491 | 0.11202 | 0.088202 | 0.070426 | 0.056323 | 0.044743 | 0.034599 | 0.025706 | 0.017637 | 0.010413 | 0 | 0 | 10.4 | 723.5367 | 897.3459 | 996.9955 | 1069.0437 | 1114.4318 | 1142.2273 | 1162.1275 | 1175.9695 | 1185.3159 | 1191.5198 | 1195.5295 | 1198.1112 | 1199.7219 | 1200.7491 | 1201.3734 | 1201.7888 | 1202.0448 | 1202.235 | 1202.3385 | 1202.4199 | 1202.0786
10.5 | 1.1503 | 0.58731 | 0.64184 | 0.67388 | 0.63002 | 0.5076 | 0.36634 | 0.26798 | 0.20018 | 0.15317 | 0.12025 | 0.096384 | 0.078533 | 0.064317 | 0.052583 | 0.042231 | 0.033078 | 0.024705 | 0.01717 | 0.010068 | 0 | 0 | 10.5 | 723.5367 | 901.9219 | 1004.3159 | 1083.2038 | 1135.0723 | 1163.0121 | 1176.8444 | 1186.185 | 1192.3851 | 1196.3912 | 1198.9687 | 1200.5736 | 1201.5925 | 1202.205 | 1202.6041 | 1202.8385 | 1203.0016 | 1203.0735 | 1203.1225 | 1203.1254 | 1202.7906
10.6 | 0.010506 | -0.45465 | -0.24139 | 0.0069016 | 0.20674 | 0.29715 | 0.27625 | 0.20847 | 0.16146 | 0.12854 | 0.10465 | 0.086769 | 0.072502 | 0.06069 | 0.050226 | 0.040918 | 0.032337 | 0.024542 | 0.017137 | 0.010181 | 0 | 0 | 10.6 | 723.5367 | 890.3624 | 988.0624 | 1070.3086 | 1131.7527 | 1169.6664 | 1187.0559 | 1193.253 | 1197.2568 | 1199.8322 | 1201.4343 | 1202.4495 | 1203.0564 | 1203.4473 | 1203.67 | 1203.8169 | 1203.8671 | 1203.8891 | 1203.8604 | 1203.8492 | 1203.4814
10.7 | -1.0242 | -1.3875 | -1.0891 | -0.7083 | -0.3258 | -0.024482 | 0.13935 | 0.16977 | 0.13685 | 0.11296 | 0.095062 | 0.080773 | 0.068928 | 0.058411 | 0.049026 | 0.040332 | 0.032382 | 0.024769 | 0.017553 | 0.010391 | 0 | 0 | 10.7 | 723.5367 | 868.8953 | 956.3407 | 1036.6099 | 1104.8984 | 1155.7905 | 1186.0695 | 1198.124 | 1200.6982 | 1202.299 | 1203.3125 | 1203.9169 | 1204.3042 | 1204.5212 | 1204.66 | 1204.6986 | 1204.7043 | 1204.654 | 1204.6157 | 1204.5618 | 1204.1946
10.8 | -1.904 | -2.1755 | -1.8537 | -1.4215 | -0.93936 | -0.48354 | -0.13094 | 0.067741 | 0.12128 | 0.10338 | 0.08908 | 0.077222 | 0.066682 | 0.057263 | 0.048517 | 0.04049 | 0.032764 | 0.025393 | 0.018023 | 0.010802 | 0 | 0 | 10.8 | 723.5367 | 843.3125 | 917.4436 | 990.9351 | 1060.6499 | 1121.3021 | 1166.8584 | 1193.5136 | 1203.1652 | 1204.1779 | 1204.7812 | 1205.167 | 1205.3816 | 1205.5168 | 1205.5497 | 1205.5474 | 1205.4854 | 1205.4309 | 1205.3554 | 1205.3177 | 1204.9184
10.9 | -2.6132 | -2.8092 | -2.5064 | -2.0839 | -1.5787 | -1.0456 | -0.55508 | -0.17942 | 0.034272 | 0.0974 | 0.085538 | 0.07499 | 0.065558 | 0.056789 | 0.048728 | 0.040949 | 0.033501 | 0.026018 | 0.018642 | 0.011113 | 0 | 0 | 10.9 | 723.5367 | 817.8752 | 877.9217 | 941.5136 | 1007.3577 | 1071.7261 | 1128.7481 | 1171.8998 | 1196.9931 | 1205.647 | 1206.0322 | 1206.2458 | 1206.3795 | 1206.41 | 1206.4041 | 1206.3365 | 1206.274 | 1206.1868 | 1206.1329 | 1206.0739 | 1205.6796
11 | -3.1604 | -3.2983 | -3.0374 | -2.6624 | -2.1893 | -1.6498 | -1.0939 | -0.58849 | -0.20329 | 0.016435 | 0.083311 | 0.073874 | 0.065097 | 0.057022 | 0.049221 | 0.041739 | 0.034203 | 0.026749 | 0.019108 | 0.011501 | 0 | 0 | 11 | 723.5367 | 795.1737 | 841.988 | 894.4144 | 952.6431 | 1014.8353 | 1076.7814 | 1132.2315 | 1174.382 | 1198.8474 | 1207.1114 | 1207.2445 | 1207.2741 | 1207.2667 | 1207.1968 | 1207.1307 | 1207.0379 | 1206.976 | 1206.9052 | 1206.8754 | 1206.4545
11.1 | -3.5676 | -3.6628 | -3.4522 | -3.1413 | -2.7322 | -2.2368 | -1.6828 | -1.1176 | -0.60627 | -0.21737 | 0.0047726 | 0.073418 | 0.065339 | 0.057529 | 0.050033 | 0.042475 | 0.034987 | 0.027293 | 0.019608 | 0.011721 | 0 | 0 | 11.1 | 723.5367 | 776.3661 | 811.734 | 853.2234 | 901.9851 | 957.7656 | 1018.3575 | 1079.2808 | 1134.0907 | 1175.847 | 1200.0598 | 1208.1397 | 1208.1317 | 1208.0608 | 1207.9932 | 1207.8981 | 1207.8326 | 1207.7563 | 1207.7184 | 1207.6732 | 1207.2628
11.2 | -3.8614 | -3.9266 | -3.7646 | -3.5204 | -3.1873 | -2.764 | -2.2596 | -1.7001 | -1.1314 | -0.61787 | -0.22725 | -0.0037618 | 0.06585 | 0.05835 | 0.050783 | 0.043282 | 0.035565 | 0.027846 | 0.019906 | 0.011995 | 0 | 0 | 11.2 | 723.5367 | 761.6342 | 787.6825 | 819.4318 | 858.471 | 905.6124 | 960.3391 | 1020.2592 | 1080.7646 | 1135.3086 | 1176.876 | 1200.9471 | 1208.9263 | 1208.8582 | 1208.7621 | 1208.6951 | 1208.6165 | 1208.575 | 1208.5243 | 1208.51 | 1208.0774
11.3 | -4.0681 | -4.1128 | -3.9931 | -3.8091 | -3.5506 | -3.2088 | -2.7802 | -2.2727 | -1.7113 | -1.1411 | -0.62635 | -0.23481 | -0.01075 | 0.059104 | 0.051599 | 0.043873 | 0.036141 | 0.028178 | 0.020233 | 0.012102 | 0 | 0 | 11.3 | 723.5367 | 750.5792 | 769.414 | 793.0612 | 823.2006 | 861.1788 | 907.6247 | 961.9001 | 1021.5212 | 1081.8131 | 1136.2017 | 1177.6634 | 1201.6736 | 1209.6275 | 1209.56 | 1209.4804 | 1209.4375 | 1209.3844 | 1209.3666 | 1209.3358 | 1208.9173
11.4 | -4.2105 | -4.2415 | -4.1558 | -4.022 | -3.8291 | -3.5653 | -3.2205 | -2.7903 | -2.2816 | -1.7193 | -1.1485 | -0.63327 | -0.24155 | -0.017501 | 0.052194 | 0.044457 | 0.036486 | 0.028527 | 0.020374 | 0.012277 | 0 | 0 | 11.4 | 723.5367 | 742.5753 | 756.0319 | 773.304 | 795.9101 | 825.3609 | 862.8781 | 908.9998 | 963.0274 | 1022.4593 | 1082.6206 | 1136.9342 | 1178.3654 | 1202.3754 | 1210.3458 | 1210.3024 | 1210.2484 | 1210.2291 | 1210.1959 | 1210.1938 | 1209.7557
11.5 | -4.3068 | -4.3289 | -4.2693 | -4.1746 | -4.0353 | -3.8393 | -3.5739 | -3.228 | -2.7972 | -2.2882 | -1.7258 | -1.155 | -0.63996 | -0.24845 | -0.024642 | 0.044808 | 0.036844 | 0.028682 | 0.020571 | 0.012304 | 0 | 0 | 11.5 | 723.5367 | 736.9423 | 746.5267 | 758.9839 | 775.5922 | 797.755 | 826.8868 | 864.1455 | 910.0522 | 963.9145 | 1023.2375 | 1083.343 | 1137.6422 | 1179.0846 | 1203.1178 | 1211.1137 | 1211.0939 | 1211.0598 | 1211.0563 | 1211.035 | 1210.613
11.6 | -4.3712 | -4.3876 | -4.3469 | -4.2817 | -4.1838 | -4.0425 | -3.8454 | -3.5793 | -3.2332 | -2.8025 | -2.294 | -1.732 | -1.1617 | -0.64704 | -0.25582 | -0.032255 | 0.037003 | 0.028888 | 0.020612 | 0.012417 | 0 | 0 | 11.6 | 723.5367 | 733.0786 | 739.9421 | 748.8972 | 760.9362 | 777.2488 | 799.1697 | 828.0912 | 865.1736 | 910.9454 | 964.7171 | 1023.9916 | 1084.0828 | 1138.3909 | 1179.8535 | 1203.9094 | 1211.9251 | 1211.9211 | 1211.8989 | 1211.9041 | 1211.4636
11.7 | -4.4138 | -4.4266 | -4.3995 | -4.3554 | -4.2881 | -4.1887 | -4.0467 | -3.8491 | -3.5831 | -3.2375 | -2.8076 | -2.2999 | -1.7386 | -1.1689 | -0.65459 | -0.26362 | -0.04021 | 0.028933 | 0.020734 | 0.012399 | 0 | 0 | 11.7 | 723.5367 | 730.4792 | 735.4843 | 741.9567 | 750.6387 | 762.4601 | 778.5849 | 800.3459 | 829.1369 | 866.1178 | 911.8151 | 965.5375 | 1024.7867 | 1084.8724 | 1139.1888 | 1180.6658 | 1204.7365 | 1212.7641 | 1212.7689 | 1212.7528 | 1212.3294
11.8 | -4.4418 | -4.4524 | -4.4346 | -4.4053 | -4.3597 | -4.2913 | -4.1914 | -4.0492 | -3.852 | -3.5868 | -3.2421 | -2.8131 | -2.3062 | -1.7457 | -1.1765 | -0.66248 | -0.27168 | -0.048364 | 0.02072 | 0.01248 | 0 | 0 | 11.8 | 723.5367 | 728.7668 | 732.5188 | 737.2711 | 743.5445 | 752.0608 | 763.746 | 779.7629 | 801.4384 | 830.1594 | 867.0801 | 912.726 | 966.4082 | 1025.6313 | 1085.7058 | 1140.0225 | 1181.5059 | 1205.5844 | 1213.618 | 1213.6271 | 1213.1857
11.9 | -4.4604 | -4.4696 | -4.458 | -4.4386 | -4.4081 | -4.3618 | -4.2931 | -4.1933 | -4.0516 | -3.8551 | -3.5908 | -3.2471 | -2.8191 | -2.313 | -1.7531 | -1.1843 | -0.67056 | -0.27988 | -0.056617 | 0.012439 | 0 | 0 | 11.9 | 723.5367 | 727.6521 | 730.5707 | 734.1385 | 738.7396 | 744.8951 | 753.3252 | 764.9485 | 780.9176 | 802.549 | 831.2233 | 868.0927 | 913.6868 | 967.3229 | 1026.5122 | 1086.5672 | 1140.877 | 1182.3609 | 1206.4426 | 1214.479 | 1214.0552
12 | -4.4729 | -4.4811 | -4.4734 | -4.4606 | -4.4403 | -4.4094 | -4.363 | -4.2946 | -4.1953 | -4.0543 | -3.8587 | -3.5952 | -3.2525 | -2.8254 | -2.3201 | -1.7608 | -1.1923 | -0.67875 | -0.28815 | -0.064915 | 0 | 0 | 12 | 723.5367 | 726.9286 | 729.2831 | 732.0611 | 735.5218 | 740.0509 | 746.1626 | 754.5664 | 766.1691 | 782.1136 | 803.7099 | 832.337 | 869.1497 | 914.6841 | 968.2661 | 1027.4141 | 1087.4438 | 1141.7421 | 1183.2231 | 1207.3055 | 1214.9138
12.1 | -4.4813 | -4.4888 | -4.4836 | -4.475 | -4.4616 | -4.4412 | -4.4104 | -4.3644 | -4.2965 | -4.1978 | -4.0575 | -3.8626 | -3.6 | -3.2581 | -2.8318 | -2.3273 | -1.7685 | -1.2004 | -0.68698 | -0.29644 | 0 | 0 | 12.1 | 723.5367 | 726.4382 | 728.4263 | 730.6812 | 733.3949 | 736.8222 | 741.3391 | 747.448 | 755.8486 | 767.4396 | 783.3592 | 804.915 | 833.4873 | 870.2352 | 915.7029 | 969.2248 | 1028.327 | 1088.3279 | 1142.612 | 1184.0883 | 1207.7348
12.2 | -4.4869 | -4.4939 | -4.4902 | -4.4845 | -4.4757 | -4.4624 | -4.4423 | -4.4119 | -4.3662 | -4.2988 | -4.2007 | -4.061 | -3.8668 | -3.605 | -3.2639 | -2.8384 | -2.3345 | -1.7762 | -1.2084 | -0.65651 | 0 | 0 | 12.2 | 723.5367 | 726.0991 | 727.8408 | 729.7699 | 731.9969 | 734.7056 | 738.1406 | 742.668 | 748.7831 | 757.1801 | 768.7541 | 784.6411 | 806.1487 | 834.6591 | 871.3366 | 916.733 | 970.1914 | 1029.2452 | 1089.2153 | 1139.4591 | 1180.5002
12.3 | -4.4907 | -4.4972 | -4.4948 | -4.4909 | -4.4852 | -4.4766 | -4.4636 | -4.4438 | -4.4137 | -4.3685 | -4.3015 | -4.2038 | -4.0647 | -3.8712 | -3.6101 | -3.2698 | -2.845 | -2.3418 | -1.7453 | -1.0428 | 0 | 0 | 12.3 | 723.5367 | 725.86 | 727.4455 | 729.1631 | 731.0908 | 733.3304 | 736.0571 | 739.5084 | 744.0461 | 750.1618 | 758.5477 | 770.0968 | 785.9445 | 807.3981 | 835.8424 | 872.4462 | 917.7688 | 971.1619 | 1026.1411 | 1072.0336 | 1125.8492
12.4 | -4.493 | -4.4994 | -4.4978 | -4.4954 | -4.4918 | -4.4863 | -4.478 | -4.4653 | -4.4457 | -4.416 | -4.371 | -4.3043 | -4.2071 | -4.0685 | -3.8756 | -3.6152 | -3.2756 | -2.813 | -2.1754 | -1.3512 | 0 | 0 | 12.4 | 723.5367 | 725.7052 | 727.1838 | 728.7708 | 730.5033 | 732.4524 | 734.7134 | 737.4576 | 740.9197 | 745.46 | 751.5686 | 759.9364 | 771.4551 | 787.2591 | 808.6557 | 837.0315 | 873.5599 | 914.7835 | 954.0652 | 985.2615 | 1044.7309
12.5 | -4.4945 | -4.5009 | -4.5001 | -4.4987 | -4.4965 | -4.4931 | -4.4879 | -4.4798 | -4.4673 | -4.4479 | -4.4184 | -4.3736 | -4.3073 | -4.2104 | -4.0723 | -3.88 | -3.5817 | -3.108 | -2.4181 | -1.5223 | 0 | 0 | 12.5 | 723.5367 | 725.6116 | 727.0312 | 728.5269 | 730.1368 | 731.8928 | 733.8627 | 736.1395 | 738.8936 | 742.3587 | 746.8948 | 752.9907 | 761.3363 | 772.8214 | 788.5795 | 809.9173 | 834.2017 | 856.6128 | 874.0301 | 886.3057 | 944.7498
12.6 | -4.4955 | -4.502 | -4.5016 | -4.5011 | -4.4999 | -4.498 | -4.4948 | -4.4898 | -4.4818 | -4.4695 | -4.4503 | -4.4209 | -4.3764 | -4.3103 | -4.2138 | -4.0376 | -3.7111 | -3.1858 | -2.4543 | -1.5474 | 0 | 0 | 12.6 | 723.5367 | 725.5713 | 726.9549 | 728.399 | 729.9192 | 731.5513 | 733.3253 | 735.3085 | 737.5933 | 740.3504 | 743.813 | 748.3406 | 754.4206 | 762.7416 | 774.1916 | 785.8843 | 793.1305 | 793.6235 | 789.0205 | 783.6796 | 836.3889
12.7 | -4.4964 | -4.5029 | -4.503 | -4.5029 | -4.5026 | -4.5016 | -4.4999 | -4.4967 | -4.4918 | -4.484 | -4.4718 | -4.4526 | -4.4234 | -4.3791 | -4.2748 | -4.0441 | -3.641 | -3.057 | -2.315 | -1.4531 | 0 | 0 | 12.7 | 723.5367 | 725.5625 | 726.9388 | 728.3482 | 729.8152 | 731.3544 | 733.0011 | 734.7854 | 736.7749 | 739.0622 | 741.818 | 745.2749 | 749.7917 | 755.8543 | 760.1356 | 757.5305 | 745.4733 | 725.7366 | 703.4728 | 685.1098 | 729.5902
12.8 | -4.4973 | -4.5039 | -4.5041 | -4.5045 | -4.5046 | -4.5044 | -4.5036 | -4.5019 | -4.4989 | -4.494 | -4.4862 | -4.4741 | -4.455 | -4.3875 | -4.209 | -3.8779 | -3.39 | -2.7704 | -2.0563 | -1.2815 | 0 | 0 | 12.8 | 723.5367 | 725.5792 | 726.9553 | 728.3556 | 729.7844 | 731.2666 | 732.817 | 734.4716 | 736.2605 | 738.2521 | 740.5387 | 743.2908 | 746.7405 | 747.2361 | 739.2769 | 719.8559 | 690.3194 | 655.5394 | 622.0405 | 596.1794 | 631.8042
12.9 | -4.4983 | -4.505 | -4.5054 | -4.5058 | -4.5063 | -4.5065 | -4.5064 | -4.5056 | -4.504 | -4.501 | -4.4962 | -4.4885 | -4.438 | -4.2849 | -3.9908 | -3.5553 | -3.0081 | -2.3901 | -1.7377 | -1.0738 | 0 | 0 | 12.9 | 723.5367 | 725.6036 | 726.9952 | 728.3916 | 729.8074 | 731.2479 | 732.7386 | 734.2946 | 735.9526 | 737.7431 | 739.7345 | 742.0187 | 740.7621 | 730.2172 | 707.0548 | 672.219 | 630.1231 | 586.8451 | 548.4524 | 520.0204 | 547.3699
13 | -4.4994 | -4.5063 | -4.5066 | -4.5072 | -4.5077 | -4.5083 | -4.5085 | -4.5085 | -4.5078 | -4.5062 | -4.5032 | -4.4601 | -4.3184 | -4.0416 | -3.6319 | -3.122 | -2.5566 | -1.9765 | -1.4086 | -0.86275 | 0 | 0 | 13 | 723.5367 | 725.6354 | 727.0389 | 728.447 | 729.8552 | 731.2797 | 732.7262 | 734.2211 | 735.7796 | 737.4389 | 739.2293 | 737.2205 | 725.533 | 700.6584 | 663.2895 | 617.5023 | 568.9548 | 523.2448 | 485.004 | 457.5708 | 477.869
13.1 | -4.5008 | -4.5077 | -4.5081 | -4.5086 | -4.5092 | -4.5098 | -4.5103 | -4.5106 | -4.5106 | -4.5099 | -4.47 | -4.3333 | -4.0642 | -3.6663 | -3.1741 | -2.6347 | -2.0919 | -1.5763 | -1.1024 | -0.66937 | 0 | 0 | 13.1 | 723.5367 | 725.6625 | 727.0861 | 728.5023 | 729.9191 | 731.3336 | 732.7626 | 734.212 | 735.7088 | 737.2682 | 734.9341 | 722.7732 | 697.1836 | 658.7223 | 611.2718 | 560.2224 | 510.8251 | 467.2926 | 432.5042 | 408.2091 | 422.8674
13.2 | -4.5023 | -4.5094 | -4.5096 | -4.5101 | -4.5106 | -4.5112 | -4.5119 | -4.5125 | -4.5128 | -4.4745 | -4.3402 | -4.0746 | -3.6821 | -3.198 | -2.6707 | -2.1456 | -1.6558 | -1.2189 | -0.83786 | -0.50452 | 0 | 0 | 13.2 | 723.5367 | 725.6898 | 727.1248 | 728.5579 | 729.9804 | 731.4018 | 732.8194 | 734.2506 | 735.7013 | 733.2108 | 720.8381 | 694.9591 | 656.0729 | 607.9551 | 555.8438 | 504.7881 | 458.7346 | 420.2246 | 390.5995 | 370.3723 | 380.7392
13.3 | -4.504 | -4.5111 | -4.5113 | -4.5116 | -4.5121 | -4.5127 | -4.5134 | -4.514 | -4.4764 | -4.3433 | -4.0797 | -3.69 | -3.2099 | -2.6882 | -2.1713 | -1.6933 | -1.2738 | -0.91816 | -0.62144 | -0.3713 | 0 | 0 | 13.3 | 723.5367 | 725.709 | 727.1606 | 728.6026 | 730.0403 | 731.4659 | 732.8895 | 734.3087 | 731.7582 | 719.2957 | 693.2955 | 654.2454 | 605.885 | 553.3788 | 501.6606 | 454.5267 | 414.3256 | 382.1427 | 358.1609 | 342.1111 | 349.3272
13.4 | -4.5058 | -4.5129 | -4.5131 | -4.5134 | -4.5137 | -4.5142 | -4.5148 | -4.4773 | -4.3447 | -4.0821 | -3.6941 | -3.2164 | -2.6978 | -2.1849 | -1.7124 | -1.3007 | -0.95656 | -0.67692 | -0.45193 | -0.26812 | 0 | 0 | 13.4 | 723.5367 | 725.7273 | 727.1857 | 728.6427 | 730.0878 | 731.5277 | 732.9549 | 730.4023 | 717.9268 | 691.9015 | 652.8091 | 604.374 | 551.7336 | 499.7773 | 452.2302 | 411.3342 | 378.0349 | 352.3297 | 333.697 | 321.4368 | 326.416
13.5 | -4.5077 | -4.5148 | -4.515 | -4.5152 | -4.5155 | -4.5158 | -4.4783 | -4.3457 | -4.0836 | -3.6965 | -3.2202 | -2.7036 | -2.1931 | -1.7236 | -1.3155 | -0.97653 | -0.7044 | -0.49069 | -0.32381 | -0.19089 | 0 | 0 | 13.5 | 723.5367 | 725.738 | 727.2083 | 728.6706 | 730.1298 | 731.5764 | 729.0455 | 716.5964 | 690.6037 | 651.5455 | 603.1317 | 550.4786 | 498.4521 | 450.7524 | 409.5861 | 375.8378 | 349.4056 | 329.6317 | 315.6308 | 306.5616 | 309.9872
13.6 | -4.5097 | -4.5168 | -4.5169 | -4.5171 | -4.5172 | -4.4795 | -4.347 | -4.085 | -3.6985 | -3.2231 | -2.7078 | -2.1987 | -1.7309 | -1.325 | -0.98862 | -0.7199 | -0.51106 | -0.35151 | -0.22977 | -0.13473 | 0 | 0 | 13.6 | 723.5367 | 725.7491 | 727.2218 | 728.6953 | 730.1591 | 727.6527 | 715.2413 | 689.3049 | 650.3201 | 601.9851 | 549.3956 | 497.395 | 449.6642 | 408.3956 | 374.459 | 347.7247 | 327.4771 | 312.7319 | 302.5106 | 295.9751 | 298.3504
13.7 | -4.5117 | -4.5188 | -4.5189 | -4.519 | -4.4812 | -4.3486 | -4.0869 | -3.7008 | -3.2261 | -2.7115 | -2.2034 | -1.7367 | -1.3319 | -0.99694 | -0.73002 | -0.52354 | -0.36724 | -0.25026 | -0.1625 | -0.094864 | 0 | 0 | 13.7 | 723.5367 | 725.7539 | 727.235 | 728.7101 | 726.2233 | 713.8473 | 687.9699 | 649.0699 | 600.8371 | 548.3506 | 496.4332 | 448.7478 | 407.473 | 373.4698 | 346.6014 | 326.1408 | 311.0764 | 300.3702 | 293.084 | 288.4852 | 290.1583
13.8 | -4.5137 | -4.5208 | -4.5208 | -4.483 | -4.3505 | -4.089 | -3.7034 | -3.2293 | -2.7155 | -2.2081 | -1.742 | -1.3379 | -1.0036 | -0.73756 | -0.53226 | -0.3776 | -0.26287 | -0.17829 | -0.11539 | -0.067171 | 0 | 0 | 13.8 | 723.5367 | 725.7605 | 727.2411 | 724.7682 | 712.4219 | 686.5984 | 647.7807 | 599.6529 | 547.2805 | 495.4698 | 447.8691 | 406.6457 | 372.6524 | 345.746 | 325.1942 | 309.9785 | 299.0483 | 291.4362 | 286.3489 | 283.1733 | 284.39
13.9 | -4.5157 | -4.5228 | -4.485 | -4.3526 | -4.0914 | -3.7063 | -3.233 | -2.7199 | -2.2131 | -1.7476 | -1.3439 | -1.0099 | -0.74417 | -0.53933 | -0.38537 | -0.27173 | -0.18873 | -0.12804 | -0.082987 | -0.04827 | 0 | 0 | 13.9 | 723.5367 | 725.762 | 723.2981 | 710.9764 | 685.2013 | 646.4601 | 598.4322 | 546.1714 | 494.4702 | 446.9654 | 405.8168 | 371.8727 | 344.986 | 324.4195 | 309.1486 | 298.1162 | 290.3462 | 285.0312 | 281.5277 | 279.3707 | 280.2896
14 | -4.5177 | -4.4871 | -4.3548 | -4.094 | -3.7094 | -3.2368 | -2.7245 | -2.2185 | -1.7535 | -1.3502 | -1.0164 | -0.75079 | -0.54602 | -0.39222 | -0.27893 | -0.19658 | -0.13693 | -0.093438 | -0.060928 | -0.035538 | 0 | 0 | 14 | 723.5367 | 721.8209 | 709.5198 | 683.7891 | 645.1194 | 597.1857 | 545.0307 | 493.4339 | 446.0226 | 404.9517 | 371.0681 | 344.2245 | 323.6826 | 308.4142 | 297.3561 | 289.5243 | 284.1033 | 280.4398 | 278.054 | 276.5943 | 277.3207

## case c)
HYDRAULIC MODELLING | [22 empty] | ADAM BABULJAK
WATER HAMMER CALCULATIONS
INPUT VALUES
t | 14 | s | time of simulation
Q | 30 | m/s | initial discharge
D | 2.67 | m | pipe diameter
H0 | 725 | m | reservoir level
e | 0.03 | m | pipe wall thickness
E | 196200000000 | N/m2 | pipe elasticity module
K | 1962000000 | N/m2 | water compressibility
θ | 0 | - | pipe inclination
L | 2040 | m | pipe length
4) velocity of water hammer propagation
|  |  | a = | 1018.8696 | m/s | ≈ | 1020 | m/s
5) Maximum pressure in the systém
v0 = | 5.3581 | m/s
ΔHmax = | 556.4914 | m
Hmax = | 1281.4914 | m
Hmin = | 168.5086 | m
WATER HAMMER CALCULATION
lambda | 0.032 | [-] | [5 empty] | D = | 2.67 | m
tclose | 8 | s | [5 empty] | a = | 1020 | m/s
M | 21 | [-] | [5 empty] | H0 = | 725 | m
N | 20 | [-] | [5 empty] | Δx | 102 | m
t | 14 | s | [5 empty] | Δt | 0.1 | s
INITIAL CONTITIONS:
INTERNAL POINTS CALCULATION
velocity [m/s] | A | [9 empty] | B | [9 empty] | C |  | head [m] | A | [9 empty] | B | [9 empty] | C
Li = | 0 | 102 | 204 | 306 | 408 | 510 | 612 | 714 | 816 | 918 | 1020 | 1122 | 1224 | 1326 | 1428 | 1530 | 1632 | 1734 | 1836 | 1938 | 2040 |  | Li = | 0 | 102 | 204 | 306 | 408 | 510 | 612 | 714 | 816 | 918 | 1020 | 1122 | 1224 | 1326 | 1428 | 1530 | 1632 | 1734 | 1836 | 1938 | 2040
profile i | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 |  | profile | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 11
t | [21 empty] | τ | t
0 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 1 | 0 | 723.5367 | 721.748 | 719.9592 | 718.1704 | 716.3816 | 714.5928 | 712.8041 | 711.0153 | 709.2265 | 707.4377 | 705.6489 | 703.8601 | 702.0714 | 700.2826 | 698.4938 | 696.705 | 694.9162 | 693.1274 | 691.3387 | 689.5499 | 687.7611
0.1 | 5.3495 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.1568 | 0.9875 | 0.1 | 723.5367 | 721.748 | 719.9592 | 718.1704 | 716.3816 | 714.5928 | 712.8041 | 711.0153 | 709.2265 | 707.4377 | 705.6489 | 703.8601 | 702.0714 | 700.2826 | 698.4938 | 696.705 | 694.9162 | 693.1274 | 691.3387 | 689.5499 | 688.6555
0.2 | 5.3452 | 5.3538 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.2538 | 5.1317 | 0.975 | 0.2 | 723.5367 | 721.3008 | 719.9592 | 718.1704 | 716.3816 | 714.5928 | 712.8041 | 711.0153 | 709.2265 | 707.4377 | 705.6489 | 703.8601 | 702.0714 | 700.2826 | 698.4938 | 696.705 | 694.9162 | 693.1274 | 691.3387 | 700.4623 | 699.5679
0.3 | 5.3431 | 5.3517 | 5.3538 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.2538 | 5.1888 | 5.0904 | 0.9625 | 0.3 | 723.5367 | 721.0786 | 719.5134 | 718.1704 | 716.3816 | 714.5928 | 712.8041 | 711.0153 | 709.2265 | 707.4377 | 705.6489 | 703.8601 | 702.0714 | 700.2826 | 698.4938 | 696.705 | 694.9162 | 693.1274 | 702.2181 | 707.2231 | 706.3617
0.4 | 5.3421 | 5.3507 | 5.3517 | 5.3538 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.2539 | 5.189 | 5.1361 | 5.044 | 0.95 | 0.4 | 723.5367 | 720.969 | 719.292 | 717.7254 | 716.3816 | 714.5928 | 712.8041 | 711.0153 | 709.2265 | 707.4377 | 705.6489 | 703.8601 | 702.0714 | 700.2826 | 698.4938 | 696.705 | 694.9162 | 703.9897 | 708.9749 | 712.7819 | 711.9072
0.5 | 5.3416 | 5.3502 | 5.3507 | 5.3517 | 5.3538 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.2541 | 5.1893 | 5.1366 | 5.0867 | 4.9959 | 0.9375 | 0.5 | 723.5367 | 720.9152 | 719.1834 | 717.5043 | 715.9373 | 714.5928 | 712.8041 | 711.0153 | 709.2265 | 707.4377 | 705.6489 | 703.8601 | 702.0714 | 700.2826 | 698.4938 | 696.705 | 705.7612 | 710.7359 | 714.5098 | 717.9787 | 717.1346
0.6 | 5.3414 | 5.3499 | 5.3502 | 5.3507 | 5.3517 | 5.3538 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.2543 | 5.1895 | 5.1371 | 5.0873 | 5.0382 | 4.9469 | 0.925 | 0.6 | 723.5367 | 720.8881 | 719.1301 | 717.3966 | 715.7165 | 714.1492 | 712.8041 | 711.0153 | 709.2265 | 707.4377 | 705.6489 | 703.8601 | 702.0714 | 700.2826 | 698.4938 | 707.5327 | 712.4968 | 716.2451 | 719.6888 | 723.1373 | 722.2787
0.7 | 5.3413 | 5.3498 | 5.3499 | 5.3502 | 5.3507 | 5.3517 | 5.3538 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.2544 | 5.1898 | 5.1376 | 5.088 | 5.039 | 4.9896 | 4.8975 | 0.9125 | 0.7 | 723.5367 | 720.8752 | 719.1033 | 717.3437 | 715.6097 | 713.9288 | 712.3611 | 711.0153 | 709.2265 | 707.4377 | 705.6489 | 703.8601 | 702.0714 | 700.2826 | 709.3043 | 714.2578 | 717.9804 | 721.4056 | 724.8314 | 728.2839 | 727.4552
0.8 | 5.3412 | 5.3498 | 5.3498 | 5.35 | 5.3502 | 5.3507 | 5.3517 | 5.3538 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.3581 | 5.2546 | 5.1901 | 5.1381 | 5.0887 | 5.0398 | 4.9905 | 4.9408 | 4.8477 | 0.9 | 0.8 | 723.5367 | 720.8683 | 719.0905 | 717.3171 | 715.5574 | 713.8229 | 712.1411 | 710.5731 | 709.2265 | 707.4377 | 705.6489 | 703.8601 | 702.0714 | 711.0759 | 716.0189 | 719.7159 | 723.1226 | 726.5321 | 729.9624 | 733.4988 | 732.6556
0.9 | 5.3412 | 5.3498 | 5.3498 | 5.3499 | 5.35 | 5.3502 | 5.3507 | 5.3517 | 5.3538 | 5.3581 | 5.3581 | 5.3581 | 5.2548 | 5.1903 | 5.1386 | 5.0894 | 5.0407 | 4.9915 | 4.9419 | 4.8916 | 4.7975 | 0.8875 | 0.9 | 723.5367 | 720.8654 | 719.0837 | 717.3044 | 715.5309 | 713.7709 | 712.036 | 710.3534 | 708.785 | 707.4377 | 705.6489 | 703.8601 | 712.8476 | 717.78 | 721.4514 | 724.8397 | 728.233 | 731.6476 | 735.162 | 738.7352 | 737.9217
1 | 5.3412 | 5.3498 | 5.3498 | 5.3498 | 5.3499 | 5.35 | 5.3503 | 5.3508 | 5.3517 | 5.3539 | 5.3581 | 5.2549 | 5.1906 | 5.1391 | 5.0901 | 5.0415 | 4.9925 | 4.943 | 4.8928 | 4.8422 | 4.7469 | 0.875 | 1 | 723.5367 | 720.8635 | 719.0808 | 717.2977 | 715.5183 | 713.7447 | 711.9845 | 710.2492 | 708.5657 | 706.9969 | 705.6489 | 714.6192 | 719.5412 | 723.1871 | 726.557 | 729.9341 | 733.3331 | 736.832 | 740.3831 | 744.0508 | 743.2229
1.1 | 5.3412 | 5.3498 | 5.3498 | 5.3498 | 5.3499 | 5.3499 | 5.35 | 5.3503 | 5.3508 | 5.3518 | 5.2509 | 5.1909 | 5.1396 | 5.0908 | 5.0424 | 4.9935 | 4.9442 | 4.8941 | 4.8436 | 4.7923 | 4.6959 | 0.8625 | 1.1 | 723.5367 | 720.863 | 719.0789 | 717.2948 | 715.5116 | 713.7322 | 711.9585 | 710.1981 | 708.4623 | 706.7779 | 715.9508 | 721.3024 | 724.9229 | 728.2745 | 731.6355 | 735.0189 | 738.5022 | 742.0378 | 745.6834 | 749.3918 | 748.5936
1.2 | 5.3413 | 5.3498 | 5.3498 | 5.3498 | 5.3499 | 5.3499 | 5.3499 | 5.3501 | 5.3503 | 5.248 | 5.1848 | 5.1359 | 5.0914 | 5.0432 | 4.9944 | 4.9453 | 4.8954 | 4.845 | 4.7938 | 4.7421 | 4.6446 | 0.85 | 1.2 | 723.5367 | 720.8623 | 719.0784 | 717.2929 | 715.5088 | 713.7256 | 711.9461 | 710.1723 | 708.4117 | 717.4004 | 722.4049 | 726.2194 | 729.9921 | 733.337 | 736.7049 | 740.1728 | 743.6929 | 747.323 | 751.0093 | 754.8138 | 754.0013
1.3 | 5.3413 | 5.3499 | 5.3499 | 5.3499 | 5.3499 | 5.3499 | 5.3499 | 5.35 | 5.2474 | 5.1836 | 5.1334 | 5.0858 | 5.0398 | 4.9954 | 4.9464 | 4.8967 | 4.8464 | 4.7953 | 4.7438 | 4.6914 | 4.5929 | 0.8375 | 1.3 | 723.5367 | 720.8624 | 719.0777 | 717.2924 | 715.5069 | 713.7227 | 711.9395 | 710.16 | 719.094 | 724.0124 | 727.6344 | 731.0521 | 734.6001 | 738.3912 | 741.8436 | 745.3483 | 748.9629 | 752.6337 | 756.4161 | 760.2625 | 759.4795
1.4 | 5.3413 | 5.3499 | 5.3499 | 5.3499 | 5.3499 | 5.3499 | 5.3499 | 5.2474 | 5.1836 | 5.1332 | 5.0851 | 5.0376 | 4.9901 | 4.9433 | 4.8979 | 4.8478 | 4.7969 | 4.7455 | 4.6932 | 4.6405 | 4.5407 | 0.825 | 1.4 | 723.5367 | 720.862 | 719.0778 | 717.2917 | 715.5064 | 713.7209 | 711.9367 | 720.8443 | 725.7336 | 729.2931 | 732.6176 | 735.9823 | 739.4211 | 743.0768 | 747.0041 | 750.6033 | 754.2585 | 758.0254 | 761.8496 | 765.7931 | 764.9958
1.5 | 5.3413 | 5.3499 | 5.3499 | 5.3499 | 5.3499 | 5.3499 | 5.2476 | 5.1838 | 5.1335 | 5.0854 | 5.0377 | 4.9897 | 4.9414 | 4.8929 | 4.845 | 4.7984 | 4.7472 | 4.6951 | 4.6424 | 4.5891 | 4.4882 | 0.8125 | 1.5 | 723.5367 | 720.8622 | 719.0774 | 717.2918 | 715.5057 | 713.7204 | 722.6088 | 727.483 | 731.0081 | 734.2959 | 737.6077 | 740.9567 | 744.4296 | 748.0046 | 751.8066 | 755.8838 | 759.6351 | 763.4438 | 767.3651 | 771.3512 | 770.5832
1.6 | 5.3414 | 5.3499 | 5.3499 | 5.3499 | 5.3499 | 5.2478 | 5.184 | 5.134 | 5.086 | 5.0384 | 4.9903 | 4.9419 | 4.8927 | 4.8434 | 4.7937 | 4.7447 | 4.6969 | 4.6444 | 4.5911 | 4.5374 | 4.4353 | 0.8 | 1.6 | 723.5367 | 720.8619 | 719.0776 | 717.2914 | 715.5058 | 724.3767 | 729.2394 | 732.7371 | 736.0022 | 739.2891 | 742.6043 | 746.0252 | 749.5111 | 753.1303 | 756.8548 | 760.8086 | 765.0385 | 768.9442 | 772.9081 | 776.9919 | 776.2098
1.7 | 5.3414 | 5.35 | 5.35 | 5.35 | 5.2479 | 5.1843 | 5.1345 | 5.0867 | 5.0392 | 4.9912 | 4.9428 | 4.8937 | 4.8441 | 4.7939 | 4.7433 | 4.6924 | 4.6422 | 4.5932 | 4.5395 | 4.4851 | 4.382 | 0.7875 | 1.7 | 723.5367 | 720.8622 | 719.0773 | 717.2916 | 726.1454 | 730.9975 | 734.4697 | 737.7156 | 740.9845 | 744.2799 | 747.6764 | 751.1288 | 754.6962 | 758.3322 | 762.103 | 765.98 | 770.0877 | 774.4722 | 778.5338 | 782.6611 | 781.9082
1.8 | 5.3414 | 5.35 | 5.35 | 5.2481 | 5.1846 | 5.1351 | 5.0874 | 5.04 | 4.9922 | 4.9439 | 4.8949 | 4.8454 | 4.7951 | 4.7443 | 4.6929 | 4.6412 | 4.5891 | 4.5376 | 4.4874 | 4.4326 | 4.3282 | 0.775 | 1.8 | 723.5367 | 720.8619 | 719.0776 | 727.9145 | 732.7561 | 736.2032 | 739.4308 | 742.6835 | 745.9625 | 749.3417 | 752.7743 | 756.3174 | 759.9199 | 763.6391 | 767.4281 | 771.3527 | 775.384 | 779.6474 | 784.188 | 788.4138 | 787.6468
1.9 | 5.3414 | 5.35 | 5.2483 | 5.1849 | 5.1356 | 5.0881 | 5.0409 | 4.9931 | 4.945 | 4.8961 | 4.8467 | 4.7965 | 4.7459 | 4.6944 | 4.6425 | 4.5898 | 4.5369 | 4.4836 | 4.4309 | 4.3795 | 4.2741 | 0.7625 | 1.9 | 723.5367 | 720.8622 | 729.6836 | 734.5148 | 737.937 | 741.1466 | 744.3836 | 747.6472 | 751.0106 | 754.427 | 757.9526 | 761.5354 | 765.2302 | 768.9858 | 772.859 | 776.8028 | 780.8829 | 785.0702 | 789.4908 | 794.1957 | 793.4577
2 | 5.3415 | 5.2485 | 5.1852 | 5.1361 | 5.0888 | 5.0417 | 4.9941 | 4.9461 | 4.8974 | 4.8481 | 4.7981 | 4.7475 | 4.6961 | 4.6443 | 4.5916 | 4.5385 | 4.4846 | 4.4305 | 4.3759 | 4.3221 | 4.2195 | 0.75 | 2 | 723.5367 | 731.4514 | 736.2737 | 739.6711 | 742.8627 | 746.0841 | 749.3325 | 752.6807 | 756.0817 | 759.5915 | 763.158 | 766.8353 | 770.5711 | 774.4199 | 778.3304 | 782.3593 | 786.4596 | 790.6968 | 795.0417 | 799.6276 | 799.3098
2.1 | 5.2401 | 5.1855 | 5.1366 | 5.0895 | 5.0426 | 4.9951 | 4.9473 | 4.8986 | 4.8495 | 4.7996 | 4.7492 | 4.6979 | 4.6462 | 4.5936 | 4.5406 | 4.4867 | 4.4323 | 4.3772 | 4.3218 | 4.2661 | 4.1634 | 0.7375 | 2.1 | 723.5367 | 738.0311 | 741.4052 | 744.5789 | 747.7849 | 751.0182 | 754.3513 | 757.7372 | 761.2317 | 764.7827 | 768.4442 | 772.1636 | 775.9948 | 779.8854 | 783.89 | 787.9571 | 792.1433 | 796.4017 | 800.7975 | 805.3081 | 804.8014
2.2 | 5.1268 | 5.0863 | 5.0902 | 5.0434 | 4.9961 | 4.9484 | 4.8999 | 4.8509 | 4.8011 | 4.7509 | 4.6998 | 4.6482 | 4.5957 | 4.5428 | 4.489 | 4.4347 | 4.3796 | 4.324 | 4.2676 | 4.2126 | 4.107 | 0.725 | 2.2 | 723.5367 | 737.8517 | 746.2954 | 749.4859 | 752.7041 | 756.0222 | 759.3931 | 762.8725 | 766.4082 | 770.0544 | 773.7582 | 777.5735 | 781.4477 | 785.4347 | 789.4819 | 793.6438 | 797.869 | 802.2141 | 806.6321 | 811.0366 | 810.3946
2.3 | 5.0221 | 4.9834 | 4.9935 | 4.9971 | 4.9495 | 4.9012 | 4.8523 | 4.8027 | 4.7525 | 4.7016 | 4.6501 | 4.5978 | 4.545 | 4.4913 | 4.4372 | 4.3822 | 4.3266 | 4.2703 | 4.2149 | 4.1587 | 4.0506 | 0.7125 | 2.3 | 723.5367 | 736.8215 | 745.9007 | 754.3903 | 757.6935 | 761.0493 | 764.5137 | 768.0343 | 771.6652 | 775.3537 | 779.1537 | 783.0122 | 786.9832 | 791.0139 | 795.1582 | 799.3636 | 803.6844 | 808.0694 | 812.4173 | 816.8637 | 816.2027
2.4 | 4.9239 | 4.8852 | 4.8908 | 4.9 | 4.9024 | 4.8537 | 4.8042 | 4.7542 | 4.7034 | 4.6521 | 4.5999 | 4.5472 | 4.4937 | 4.4397 | 4.3848 | 4.3294 | 4.2731 | 4.2178 | 4.1616 | 4.1043 | 3.9941 | 0.7 | 2.4 | 723.5367 | 736.2038 | 744.8959 | 754.0868 | 762.7059 | 766.1553 | 769.6608 | 773.2766 | 776.9499 | 780.7345 | 784.5777 | 788.5332 | 792.5483 | 796.6765 | 800.8654 | 805.1686 | 809.5338 | 813.8576 | 818.2649 | 822.8505 | 822.152
2.5 | 4.8292 | 4.7902 | 4.7923 | 4.7966 | 4.8046 | 4.8058 | 4.7559 | 4.7052 | 4.654 | 4.602 | 4.5495 | 4.4961 | 4.4422 | 4.3875 | 4.3322 | 4.276 | 4.2209 | 4.1647 | 4.1075 | 4.0491 | 3.9372 | 0.6875 | 2.5 | 723.5367 | 735.9343 | 744.3785 | 753.1988 | 762.5269 | 771.2878 | 774.8884 | 778.5466 | 782.3159 | 786.1438 | 790.084 | 794.0836 | 798.1964 | 802.3696 | 806.6568 | 811.0054 | 815.3119 | 819.6996 | 824.2548 | 828.9163 | 828.2346
2.6 | 4.7362 | 4.6967 | 4.6966 | 4.6974 | 4.7004 | 4.7071 | 4.707 | 4.656 | 4.6041 | 4.5517 | 4.4985 | 4.4447 | 4.3901 | 4.335 | 4.279 | 4.2239 | 4.1679 | 4.1108 | 4.0525 | 3.9935 | 3.88 | 0.675 | 2.6 | 723.5367 | 735.8786 | 744.234 | 752.8139 | 761.7676 | 771.2382 | 780.1437 | 783.8979 | 787.7106 | 791.6354 | 795.6197 | 799.7171 | 803.8749 | 808.1465 | 812.4795 | 816.7701 | 821.1415 | 825.6795 | 830.315 | 835.0957 | 834.3942
2.7 | 4.6438 | 4.6036 | 4.6023 | 4.6009 | 4.6004 | 4.6021 | 4.6075 | 4.6062 | 4.5539 | 4.5008 | 4.4472 | 4.3928 | 4.3378 | 4.2819 | 4.227 | 4.1711 | 4.1141 | 4.0559 | 3.997 | 3.9372 | 3.8224 | 0.6625 | 2.7 | 723.5367 | 735.9453 | 744.3103 | 752.8051 | 761.5197 | 770.61 | 780.2255 | 789.2779 | 793.1875 | 797.1565 | 801.2385 | 805.3809 | 809.6372 | 813.9547 | 818.23 | 822.5859 | 827.1082 | 831.7275 | 836.4843 | 841.3228 | 840.6468
2.8 | 4.5512 | 4.5104 | 4.5085 | 4.5059 | 4.5032 | 4.5013 | 4.5017 | 4.5058 | 4.5032 | 4.4497 | 4.3954 | 4.3405 | 4.2848 | 4.2301 | 4.1743 | 4.1174 | 4.0594 | 4.0006 | 3.9408 | 3.8805 | 3.7643 | 0.65 | 2.8 | 723.5367 | 736.0769 | 744.5112 | 753.0176 | 761.649 | 770.501 | 779.7303 | 789.4926 | 798.6939 | 802.7606 | 806.8877 | 811.1286 | 815.4307 | 819.6908 | 824.0315 | 828.5386 | 833.1425 | 837.8835 | 842.6993 | 847.6452 | 846.9538
2.9 | 4.4582 | 4.4167 | 4.4145 | 4.4113 | 4.4074 | 4.4033 | 4.4001 | 4.3991 | 4.4019 | 4.398 | 4.3433 | 4.2877 | 4.2331 | 4.1775 | 4.1208 | 4.0629 | 4.0042 | 3.9446 | 3.8843 | 3.8232 | 3.7058 | 0.6375 | 2.9 | 723.5367 | 736.2436 | 744.778 | 753.3549 | 761.9997 | 770.77 | 779.7616 | 789.1319 | 799.0432 | 808.3952 | 812.6208 | 816.9075 | 821.1525 | 825.4779 | 829.97 | 834.5587 | 839.2844 | 844.0847 | 849.0083 | 854.0054 | 853.3416
3 | 4.3645 | 4.3224 | 4.32 | 4.3165 | 4.3119 | 4.3067 | 4.3013 | 4.2967 | 4.2943 | 4.2959 | 4.2906 | 4.2362 | 4.1807 | 4.1241 | 4.0663 | 4.0078 | 3.9483 | 3.8882 | 3.8271 | 3.7656 | 3.6468 | 0.625 | 3 | 723.5367 | 736.4278 | 745.0806 | 753.7588 | 762.4749 | 771.2602 | 780.1717 | 789.3049 | 798.8185 | 808.8806 | 818.3851 | 822.615 | 826.9253 | 831.4023 | 835.9759 | 840.6864 | 845.4714 | 850.3797 | 855.3549 | 860.4557 | 859.7776
3.1 | 4.2702 | 4.2274 | 4.2249 | 4.2212 | 4.2163 | 4.2104 | 4.2038 | 4.1971 | 4.1911 | 4.1874 | 4.1891 | 4.1838 | 4.1274 | 4.0698 | 4.0114 | 3.952 | 3.892 | 3.8311 | 3.7696 | 3.7073 | 3.5874 | 0.6125 | 3.1 | 723.5367 | 736.6224 | 745.4016 | 754.1988 | 763.0173 | 771.8749 | 780.8028 | 789.8575 | 799.1346 | 808.7934 | 818.8521 | 828.3734 | 832.8354 | 837.394 | 842.0893 | 846.8591 | 851.7522 | 856.7121 | 861.7912 | 866.9417 | 866.2914
3.2 | 4.175 | 4.1316 | 4.129 | 4.1252 | 4.1201 | 4.1139 | 4.1067 | 4.0987 | 4.0906 | 4.0847 | 4.0809 | 4.0806 | 4.0732 | 4.015 | 3.9557 | 3.8959 | 3.8351 | 3.7738 | 3.7115 | 3.6488 | 3.5275 | 0.6 | 3.2 | 723.5367 | 736.8218 | 745.7335 | 754.658 | 763.5963 | 772.5573 | 781.5584 | 790.631 | 799.831 | 809.0981 | 818.7667 | 829.05 | 838.8129 | 843.4931 | 848.2478 | 853.1257 | 858.0705 | 863.1344 | 868.2633 | 873.5168 | 872.8526
3.3 | 4.0791 | 4.035 | 4.0324 | 4.0285 | 4.0233 | 4.0169 | 4.0093 | 4.0007 | 3.9929 | 3.9847 | 3.9767 | 3.9707 | 3.9685 | 3.9595 | 3.8997 | 3.8391 | 3.7779 | 3.7158 | 3.6531 | 3.5896 | 3.4671 | 0.5875 | 3.3 | 723.5367 | 737.0251 | 746.0712 | 755.1287 | 764.1952 | 773.2766 | 782.3822 | 791.5289 | 800.5926 | 809.8025 | 819.2877 | 829.1911 | 839.685 | 849.6373 | 854.5001 | 859.4297 | 864.4786 | 869.5924 | 874.8245 | 880.1276 | 879.4911
3.4 | 3.9823 | 3.9375 | 3.9349 | 3.931 | 3.9257 | 3.9192 | 3.9114 | 3.9039 | 3.8953 | 3.8854 | 3.875 | 3.8651 | 3.8573 | 3.8536 | 3.8431 | 3.782 | 3.72 | 3.6575 | 3.594 | 3.53 | 3.4062 | 0.575 | 3.4 | 723.5367 | 737.2301 | 746.4132 | 755.6061 | 764.8062 | 774.0167 | 783.2433 | 792.34 | 801.4971 | 810.7799 | 820.2247 | 829.9139 | 839.9998 | 850.669 | 860.79 | 865.8237 | 870.9225 | 876.1396 | 881.4214 | 886.8278 | 886.1774
3.5 | 3.8847 | 3.8392 | 3.8366 | 3.8326 | 3.8273 | 3.8207 | 3.8143 | 3.8064 | 3.7969 | 3.786 | 3.7742 | 3.7621 | 3.7506 | 3.7413 | 3.7362 | 3.7243 | 3.6618 | 3.5985 | 3.5346 | 3.4699 | 3.3448 | 0.5625 | 3.5 | 723.5367 | 737.4373 | 746.758 | 756.0884 | 765.4247 | 774.7694 | 783.9707 | 793.2075 | 802.5233 | 811.9156 | 821.4031 | 831.0303 | 840.8885 | 851.1365 | 861.9696 | 872.2536 | 877.4557 | 882.7227 | 888.1079 | 893.5643 | 892.9416
3.6 | 3.7861 | 3.74 | 3.7374 | 3.7334 | 3.728 | 3.7229 | 3.7162 | 3.7077 | 3.6976 | 3.6862 | 3.6736 | 3.6602 | 3.6466 | 3.6336 | 3.6229 | 3.6163 | 3.603 | 3.5392 | 3.4746 | 3.4094 | 3.283 | 0.55 | 3.6 | 723.5367 | 737.6455 | 747.1055 | 756.5744 | 766.0488 | 775.3754 | 784.7299 | 794.1499 | 803.6216 | 813.1418 | 822.7166 | 832.3738 | 842.1631 | 852.1793 | 862.5839 | 873.5787 | 884.0249 | 889.3953 | 894.8308 | 900.3909 | 899.7542
3.7 | 3.6868 | 3.64 | 3.6373 | 3.6333 | 3.6294 | 3.624 | 3.6167 | 3.6078 | 3.5974 | 3.5857 | 3.5726 | 3.5586 | 3.5437 | 3.5286 | 3.5142 | 3.502 | 3.4941 | 3.4793 | 3.4142 | 3.3482 | 3.2206 | 0.5375 | 3.7 | 723.5367 | 737.8552 | 747.455 | 757.0636 | 766.5225 | 776.0062 | 785.551 | 795.1398 | 804.7637 | 814.4174 | 824.1071 | 833.8442 | 843.6601 | 853.6062 | 863.7781 | 874.3389 | 885.4955 | 896.1045 | 901.6437 | 907.2545 | 906.6452
3.8 | 3.5865 | 3.539 | 3.5363 | 3.5338 | 3.5296 | 3.5237 | 3.5161 | 3.5069 | 3.4963 | 3.4843 | 3.4711 | 3.4566 | 3.4411 | 3.4248 | 3.4082 | 3.3923 | 3.3787 | 3.3693 | 3.3532 | 3.2867 | 3.1577 | 0.525 | 3.8 | 723.5367 | 738.066 | 747.8066 | 757.401 | 767.0186 | 776.6951 | 786.4126 | 796.1605 | 805.9308 | 815.7235 | 825.5391 | 835.3874 | 845.2815 | 855.254 | 865.3562 | 875.6843 | 886.4021 | 897.7213 | 908.4939 | 914.2088 | 913.5855
3.9 | 3.4852 | 3.4371 | 3.4359 | 3.4331 | 3.4285 | 3.4222 | 3.4143 | 3.4049 | 3.3942 | 3.3821 | 3.3687 | 3.354 | 3.338 | 3.3211 | 3.3033 | 3.2854 | 3.268 | 3.2529 | 3.2421 | 3.2246 | 3.0944 | 0.5125 | 3.9 | 723.5367 | 738.2781 | 748.0055 | 757.7597 | 767.5713 | 777.4221 | 787.301 | 797.1992 | 807.1154 | 817.047 | 826.9979 | 836.9701 | 846.9748 | 857.0253 | 867.1548 | 877.414 | 887.8993 | 898.7751 | 910.2577 | 921.2009 | 920.6048
4 | 3.3831 | 3.3357 | 3.3343 | 3.331 | 3.326 | 3.3195 | 3.3115 | 3.302 | 3.2912 | 3.279 | 3.2654 | 3.2505 | 3.2344 | 3.217 | 3.1986 | 3.1794 | 3.16 | 3.1412 | 3.1246 | 3.1125 | 3.0305 | 0.5 | 4 | 723.5367 | 738.3368 | 748.2249 | 758.1741 | 768.161 | 778.1743 | 788.2051 | 798.2516 | 808.3105 | 818.3843 | 828.472 | 838.5789 | 848.7072 | 858.8687 | 869.0765 | 879.3639 | 889.7813 | 900.4248 | 911.4596 | 923.1125 | 927.6743
4.1 | 3.2815 | 3.2332 | 3.2313 | 3.2277 | 3.2225 | 3.2158 | 3.2076 | 3.1981 | 3.1872 | 3.1749 | 3.1613 | 3.1463 | 3.13 | 3.1124 | 3.0936 | 3.0737 | 3.0531 | 3.0322 | 3.0119 | 2.9939 | 2.9578 | 0.4875 | 4.1 | 723.5367 | 738.4153 | 748.4993 | 758.6246 | 768.7748 | 778.941 | 789.1213 | 799.3122 | 809.5157 | 819.7302 | 829.9594 | 840.2027 | 850.466 | 860.7513 | 871.0706 | 881.4367 | 891.8831 | 902.4596 | 913.2623 | 924.4631 | 929.6565
4.2 | 3.1795 | 3.13 | 3.127 | 3.1232 | 3.1178 | 3.111 | 3.1028 | 3.0932 | 3.0822 | 3.0699 | 3.0562 | 3.0411 | 3.0246 | 3.0069 | 2.9878 | 2.9676 | 2.9462 | 2.9241 | 2.9018 | 2.9007 | 2.8809 | 0.475 | 4.2 | 723.5367 | 738.6251 | 748.809 | 759.0983 | 769.4023 | 779.7188 | 790.0445 | 800.3812 | 810.7271 | 821.0855 | 831.4551 | 841.8403 | 852.2401 | 862.6608 | 873.1041 | 883.5823 | 894.1078 | 904.7141 | 915.4506 | 924.2675 | 928.9337
4.3 | 3.0762 | 3.0257 | 3.0223 | 3.0175 | 3.0121 | 3.0052 | 2.997 | 2.9873 | 2.9763 | 2.9639 | 2.9501 | 2.9349 | 2.9184 | 2.9005 | 2.8813 | 2.8608 | 2.839 | 2.8163 | 2.8133 | 2.8215 | 2.8031 | 0.4625 | 4.3 | 723.5367 | 738.8986 | 749.2181 | 759.5849 | 770.0399 | 780.5028 | 790.9752 | 801.4553 | 811.9464 | 822.4469 | 832.9607 | 843.4864 | 854.0285 | 864.5859 | 875.1651 | 885.7674 | 896.4055 | 907.0912 | 915.7104 | 923.2781 | 927.6297
4.4 | 2.9715 | 2.9202 | 2.9167 | 2.9116 | 2.9054 | 2.8985 | 2.8902 | 2.8804 | 2.8694 | 2.8569 | 2.843 | 2.8277 | 2.8111 | 2.7931 | 2.7738 | 2.7531 | 2.7311 | 2.7285 | 2.7363 | 2.7462 | 2.7255 | 0.45 | 4.4 | 723.5367 | 739.1815 | 749.6684 | 760.1579 | 770.6831 | 781.2934 | 791.9102 | 802.5364 | 813.1707 | 823.8166 | 834.4727 | 845.143 | 855.8257 | 866.5259 | 877.2419 | 887.9807 | 898.743 | 907.3957 | 914.9128 | 922.2 | 926.4094
4.5 | 2.8654 | 2.8133 | 2.8099 | 2.8049 | 2.7983 | 2.7907 | 2.7823 | 2.7725 | 2.7614 | 2.7489 | 2.7349 | 2.7196 | 2.7029 | 2.6848 | 2.6653 | 2.6445 | 2.643 | 2.6515 | 2.6617 | 2.6712 | 2.6484 | 0.4375 | 4.5 | 723.5367 | 739.4531 | 750.1152 | 760.7646 | 771.409 | 782.0876 | 792.8513 | 803.6217 | 814.4023 | 825.1916 | 835.9936 | 846.8062 | 857.6341 | 868.4751 | 879.3344 | 890.21 | 898.9648 | 906.5611 | 913.8822 | 921.2183 | 925.376
4.6 | 2.758 | 2.705 | 2.7019 | 2.697 | 2.6905 | 2.6825 | 2.6734 | 2.6636 | 2.6524 | 2.6398 | 2.6258 | 2.6104 | 2.5936 | 2.5754 | 2.5559 | 2.5555 | 2.5652 | 2.5764 | 2.5866 | 2.5955 | 2.5714 | 0.425 | 4.6 | 723.5367 | 739.7111 | 750.5433 | 761.3644 | 772.1668 | 782.9641 | 793.7959 | 804.7135 | 815.6384 | 826.5746 | 837.52 | 848.4791 | 859.4495 | 870.4361 | 881.4363 | 890.313 | 898.0249 | 905.4507 | 912.8661 | 920.3209 | 924.4821
4.7 | 2.6492 | 2.5956 | 2.5925 | 2.5879 | 2.5816 | 2.5737 | 2.5642 | 2.5536 | 2.5424 | 2.5297 | 2.5156 | 2.5002 | 2.4833 | 2.4651 | 2.466 | 2.4768 | 2.4892 | 2.5005 | 2.5104 | 2.5192 | 2.4947 | 0.4125 | 4.7 | 723.5367 | 739.9565 | 750.9543 | 761.9435 | 772.9171 | 783.8723 | 794.8231 | 805.809 | 816.8817 | 827.9623 | 839.0551 | 850.1579 | 861.2753 | 872.4044 | 881.4097 | 889.2484 | 896.7985 | 904.3321 | 911.8899 | 919.4607 | 923.6527
4.8 | 2.5393 | 2.4849 | 2.482 | 2.4774 | 2.4713 | 2.4636 | 2.4542 | 2.4433 | 2.4313 | 2.4185 | 2.4044 | 2.3889 | 2.3719 | 2.3741 | 2.3863 | 2.3999 | 2.4124 | 2.4235 | 2.4333 | 2.4422 | 2.418 | 0.4 | 4.8 | 723.5367 | 740.1944 | 751.351 | 762.5052 | 773.6466 | 784.7733 | 795.8822 | 806.9877 | 818.129 | 829.3579 | 840.5954 | 851.846 | 863.1072 | 872.2444 | 880.2143 | 887.8954 | 895.558 | 903.2409 | 910.9272 | 918.5888 | 922.8289
4.9 | 2.4282 | 2.3731 | 2.3702 | 2.3658 | 2.3598 | 2.3522 | 2.343 | 2.3322 | 2.3198 | 2.3063 | 2.2921 | 2.2765 | 2.28 | 2.2935 | 2.3083 | 2.3221 | 2.3344 | 2.3455 | 2.3555 | 2.3649 | 2.3414 | 0.3875 | 4.9 | 723.5367 | 740.4262 | 751.7397 | 763.0523 | 774.3591 | 785.6538 | 796.9348 | 808.1987 | 819.4601 | 830.7579 | 842.1442 | 853.5396 | 862.8114 | 870.9152 | 878.7305 | 886.5267 | 894.3412 | 902.1564 | 909.9403 | 917.6734 | 921.968
5 | 2.316 | 2.2601 | 2.2573 | 2.2529 | 2.247 | 2.2395 | 2.2305 | 2.2198 | 2.2075 | 2.1937 | 2.1787 | 2.1835 | 2.1983 | 2.2145 | 2.2295 | 2.2431 | 2.2554 | 2.2667 | 2.2772 | 2.2873 | 2.2647 | 0.375 | 5 | 723.5367 | 740.6559 | 752.1222 | 763.592 | 775.0574 | 786.5179 | 797.9672 | 809.4037 | 820.8238 | 832.2423 | 843.6977 | 853.1062 | 861.3463 | 869.2983 | 877.2306 | 885.1801 | 893.1286 | 901.0438 | 908.9031 | 916.6898 | 921.0448
5.1 | 2.2026 | 2.146 | 2.1432 | 2.1388 | 2.1329 | 2.1255 | 2.1166 | 2.1061 | 2.094 | 2.0802 | 2.0854 | 2.1008 | 2.1182 | 2.1346 | 2.1494 | 2.163 | 2.1755 | 2.1874 | 2.1986 | 2.2095 | 2.188 | 0.3625 | 5.1 | 723.5367 | 740.8833 | 752.5031 | 764.1257 | 775.7488 | 787.3683 | 798.984 | 810.589 | 822.1822 | 833.7596 | 843.2014 | 851.5034 | 859.5943 | 867.665 | 875.7518 | 883.8363 | 891.886 | 899.8784 | 907.7938 | 915.6256 | 920.0419
5.2 | 2.0881 | 2.0308 | 2.0279 | 2.0235 | 2.0177 | 2.0103 | 2.0015 | 1.9911 | 1.9791 | 1.986 | 2.0026 | 2.0203 | 2.0373 | 2.0534 | 2.0682 | 2.0821 | 2.0952 | 2.1077 | 2.1198 | 2.1315 | 2.1113 | 0.35 | 5.2 | 723.5367 | 741.1113 | 752.882 | 764.6585 | 776.4348 | 788.2126 | 799.9874 | 811.7593 | 823.5212 | 833.1389 | 841.5647 | 849.691 | 857.8256 | 866.0518 | 874.2746 | 882.4614 | 890.5894 | 898.6392 | 906.6016 | 914.4695 | 918.95
5.3 | 1.9724 | 1.9143 | 1.9114 | 1.9071 | 1.9012 | 1.8939 | 1.8851 | 1.8748 | 1.8834 | 1.9017 | 1.9212 | 1.9393 | 1.9557 | 1.9711 | 1.9863 | 2.0007 | 2.0145 | 2.0278 | 2.0408 | 2.0535 | 2.0346 | 0.3375 | 5.3 | 723.5367 | 741.3383 | 753.262 | 765.1897 | 777.1205 | 789.0517 | 800.9853 | 812.9166 | 822.714 | 831.326 | 839.63 | 847.8905 | 856.1527 | 864.4394 | 872.7653 | 881.0313 | 889.2178 | 897.3158 | 905.3157 | 913.2171 | 917.7613
5.4 | 1.8555 | 1.7967 | 1.7938 | 1.7894 | 1.7836 | 1.7762 | 1.7675 | 1.7776 | 1.7976 | 1.8188 | 1.8386 | 1.8567 | 1.8733 | 1.8888 | 1.9037 | 1.9189 | 1.9335 | 1.9478 | 1.9617 | 1.9754 | 1.9579 | 0.325 | 5.4 | 723.5367 | 741.5669 | 753.6415 | 765.7227 | 777.8049 | 789.8912 | 801.9785 | 811.9385 | 820.7215 | 829.2069 | 837.6553 | 846.096 | 854.5084 | 862.8701 | 871.1998 | 879.5253 | 887.761 | 895.8976 | 903.9324 | 911.8617 | 916.4719
5.5 | 1.7374 | 1.6779 | 1.675 | 1.6706 | 1.6647 | 1.6574 | 1.669 | 1.6905 | 1.7132 | 1.7347 | 1.7545 | 1.7729 | 1.79 | 1.8061 | 1.8216 | 1.8368 | 1.8523 | 1.8676 | 1.8825 | 1.8972 | 1.8811 | 0.3125 | 5.5 | 723.5367 | 741.7949 | 754.0233 | 766.2556 | 778.4919 | 790.7299 | 800.8433 | 809.7839 | 818.4336 | 827.0547 | 835.6773 | 844.2775 | 852.8174 | 861.2726 | 869.6337 | 877.9331 | 886.2084 | 894.381 | 902.4449 | 910.4018 | 915.0768
5.6 | 1.6181 | 1.5578 | 1.5549 | 1.5505 | 1.5446 | 1.5577 | 1.5806 | 1.6048 | 1.6278 | 1.6491 | 1.6691 | 1.6879 | 1.7059 | 1.723 | 1.7394 | 1.7552 | 1.771 | 1.7873 | 1.8032 | 1.8189 | 1.8044 | 0.3 | 5.6 | 723.5367 | 742.0249 | 754.4049 | 766.7913 | 779.179 | 789.4433 | 798.536 | 807.3408 | 816.1211 | 824.9084 | 833.6811 | 842.4026 | 851.0455 | 859.5846 | 868.0094 | 876.3205 | 884.5565 | 892.7592 | 900.8519 | 908.8319 | 913.574
5.7 | 1.4975 | 1.4366 | 1.4336 | 1.4292 | 1.4437 | 1.4681 | 1.4937 | 1.5181 | 1.5409 | 1.5624 | 1.5827 | 1.6023 | 1.6211 | 1.6392 | 1.6568 | 1.6738 | 1.6903 | 1.7068 | 1.7239 | 1.7407 | 1.7277 | 0.2875 | 5.7 | 723.5367 | 742.2544 | 754.7891 | 767.3273 | 777.7424 | 786.9862 | 795.9433 | 804.8773 | 813.8202 | 822.752 | 831.638 | 840.4531 | 849.1737 | 857.7859 | 866.2749 | 874.6363 | 882.8747 | 891.0309 | 899.1479 | 907.1512 | 911.9591
5.8 | 1.3757 | 1.314 | 1.3111 | 1.3271 | 1.3528 | 1.3799 | 1.4057 | 1.43 | 1.4529 | 1.4747 | 1.4957 | 1.516 | 1.5358 | 1.5551 | 1.5738 | 1.592 | 1.6098 | 1.6271 | 1.6445 | 1.6624 | 1.651 | 0.275 | 5.8 | 723.5367 | 742.486 | 755.1732 | 765.7402 | 775.1357 | 784.2451 | 793.3316 | 802.4273 | 811.5126 | 820.554 | 829.5279 | 838.4128 | 847.1972 | 855.8675 | 864.4163 | 872.8327 | 881.1143 | 889.2669 | 897.3321 | 905.3545 | 910.2305
5.9 | 1.2527 | 1.1902 | 1.2077 | 1.2349 | 1.2634 | 1.2906 | 1.3163 | 1.3406 | 1.3639 | 1.3863 | 1.4081 | 1.4294 | 1.4502 | 1.4706 | 1.4905 | 1.51 | 1.529 | 1.5475 | 1.5657 | 1.5841 | 1.5744 | 0.2625 | 5.9 | 723.5367 | 742.717 | 753.4346 | 762.9831 | 772.2457 | 781.4852 | 790.7336 | 799.9714 | 809.1654 | 818.2927 | 827.3329 | 836.2759 | 845.1104 | 853.8313 | 862.4289 | 870.8978 | 879.2284 | 887.419 | 895.4755 | 903.4411 | 908.384
6 | 1.1283 | 1.0855 | 1.1142 | 1.1441 | 1.1728 | 1.1999 | 1.2257 | 1.2504 | 1.2743 | 1.2975 | 1.3202 | 1.3425 | 1.3643 | 1.3858 | 1.4069 | 1.4276 | 1.4479 | 1.4678 | 1.4873 | 1.5065 | 1.4978 | 0.25 | 6 | 723.5367 | 740.8256 | 750.5259 | 759.9429 | 769.3366 | 778.7386 | 788.1294 | 797.4759 | 806.7556 | 815.9482 | 825.0446 | 834.0343 | 842.9138 | 851.6755 | 860.3165 | 868.8282 | 877.2061 | 885.4406 | 893.5302 | 901.4821 | 906.4179
6.1 | 1.023 | 0.99072 | 1.0221 | 1.0523 | 1.0808 | 1.108 | 1.1342 | 1.1595 | 1.1841 | 1.2083 | 1.232 | 1.2553 | 1.2782 | 1.3008 | 1.323 | 1.345 | 1.3666 | 1.3878 | 1.4087 | 1.4292 | 1.4213 | 0.2375 | 6.1 | 723.5367 | 737.7639 | 747.3342 | 756.8833 | 766.44 | 775.985 | 785.485 | 794.9175 | 804.2626 | 813.5113 | 822.6534 | 831.6862 | 840.603 | 849.4026 | 858.0785 | 866.6283 | 875.0439 | 883.3208 | 891.4494 | 899.4294 | 904.4041
6.2 | 0.93784 | 0.90751 | 0.92893 | 0.95895 | 0.9876 | 1.0152 | 1.0419 | 1.068 | 1.0936 | 1.1187 | 1.1435 | 1.1678 | 1.1918 | 1.2155 | 1.239 | 1.2621 | 1.285 | 1.3076 | 1.3299 | 1.3515 | 1.3449 | 0.225 | 6.2 | 723.5367 | 735.4812 | 744.1228 | 753.8355 | 763.5357 | 773.1904 | 782.777 | 792.2755 | 801.677 | 810.9715 | 820.1565 | 829.2258 | 838.1787 | 847.0096 | 855.7181 | 864.2978 | 872.7467 | 881.0563 | 889.2223 | 897.2711 | 902.3286
6.3 | 0.86473 | 0.83387 | 0.84445 | 0.86436 | 0.89341 | 0.92163 | 0.94919 | 0.97621 | 1.0028 | 1.0289 | 1.0547 | 1.0802 | 1.1053 | 1.1302 | 1.1548 | 1.1791 | 1.2033 | 1.2272 | 1.2505 | 1.2733 | 1.2687 | 0.2125 | 6.3 | 723.5367 | 734.2931 | 741.9844 | 750.7792 | 760.5896 | 770.3314 | 779.9845 | 789.54 | 798.988 | 808.3259 | 817.5475 | 826.6527 | 835.6361 | 844.4978 | 853.2327 | 861.8401 | 870.3139 | 878.6518 | 886.8804 | 894.9912 | 900.1403
6.4 | 0.79714 | 0.76544 | 0.76941 | 0.779 | 0.79849 | 0.82752 | 0.85601 | 0.88402 | 0.91163 | 0.93886 | 0.96575 | 0.99233 | 1.0186 | 1.0447 | 1.0705 | 1.096 | 1.1214 | 1.1463 | 1.1707 | 1.1949 | 1.1925 | 0.2 | 6.4 | 723.5367 | 733.815 | 740.9509 | 748.7417 | 757.5783 | 767.3872 | 777.0979 | 786.7005 | 796.1924 | 805.5675 | 814.8255 | 823.9613 | 832.9754 | 841.8627 | 850.6234 | 859.2523 | 867.7489 | 876.1416 | 884.4232 | 892.565 | 897.806
6.5 | 0.7315 | 0.69917 | 0.70008 | 0.70362 | 0.71321 | 0.73297 | 0.76246 | 0.79153 | 0.82021 | 0.84856 | 0.87658 | 0.90432 | 0.93179 | 0.95902 | 0.98604 | 1.0129 | 1.0392 | 1.0651 | 1.0908 | 1.1164 | 1.1164 | 0.1875 | 6.5 | 723.5367 | 733.6858 | 740.5732 | 747.7524 | 755.5422 | 764.348 | 774.1064 | 783.7536 | 793.2833 | 802.6953 | 811.9846 | 821.1516 | 830.1914 | 839.1044 | 847.8858 | 856.5357 | 865.0837 | 873.5239 | 881.8287 | 889.9824 | 895.3087
6.6 | 0.66622 | 0.63356 | 0.63346 | 0.63436 | 0.63818 | 0.64824 | 0.66859 | 0.69874 | 0.72855 | 0.75803 | 0.78722 | 0.81614 | 0.84482 | 0.87327 | 0.90155 | 0.92931 | 0.95666 | 0.9838 | 1.0109 | 1.0381 | 1.0404 | 0.175 | 6.6 | 723.5367 | 733.6881 | 740.4874 | 747.3752 | 754.5243 | 762.2641 | 771.0067 | 780.6922 | 790.2596 | 799.7036 | 809.0247 | 818.2179 | 827.284 | 836.2179 | 845.0202 | 853.7207 | 862.3142 | 870.7743 | 879.0856 | 887.2367 | 892.6459
6.7 | 0.60082 | 0.56807 | 0.5679 | 0.56808 | 0.56946 | 0.57387 | 0.5846 | 0.60569 | 0.63665 | 0.66731 | 0.69768 | 0.72782 | 0.75772 | 0.78743 | 0.81664 | 0.84542 | 0.874 | 0.90255 | 0.93115 | 0.95984 | 0.96459 | 0.1625 | 6.7 | 723.5367 | 733.7154 | 740.4898 | 747.26 | 754.0985 | 761.185 | 768.8526 | 777.5156 | 787.1155 | 796.5919 | 805.94 | 815.1601 | 824.2477 | 833.203 | 842.056 | 850.802 | 859.4146 | 867.8794 | 876.1849 | 884.3306 | 889.8173
6.8 | 0.53529 | 0.50263 | 0.50275 | 0.50304 | 0.50381 | 0.50588 | 0.51104 | 0.52258 | 0.54452 | 0.57637 | 0.60798 | 0.63934 | 0.67052 | 0.70117 | 0.7314 | 0.76141 | 0.79141 | 0.82144 | 0.85156 | 0.88178 | 0.8889 | 0.15 | 6.8 | 723.5367 | 733.7246 | 740.4875 | 747.2134 | 753.9214 | 760.6883 | 767.6958 | 775.2782 | 783.8505 | 793.3546 | 802.7302 | 811.9726 | 821.0821 | 830.0889 | 838.988 | 847.7532 | 856.3705 | 864.8286 | 873.127 | 881.2625 | 886.8267
6.9 | 0.46981 | 0.43735 | 0.43782 | 0.43853 | 0.43951 | 0.44103 | 0.44391 | 0.44993 | 0.46237 | 0.48526 | 0.51811 | 0.55075 | 0.58287 | 0.61456 | 0.64603 | 0.67746 | 0.70894 | 0.7405 | 0.77215 | 0.8039 | 0.81337 | 0.1375 | 6.9 | 723.5367 | 733.7042 | 740.4476 | 747.149 | 753.8034 | 760.4329 | 767.1152 | 774.0326 | 781.5196 | 789.9914 | 799.3899 | 808.655 | 817.8166 | 826.87 | 835.789 | 844.5594 | 853.1703 | 861.6212 | 869.9088 | 878.0361 | 883.6746
7 | 0.40456 | 0.37237 | 0.37317 | 0.37432 | 0.37578 | 0.37758 | 0.37996 | 0.38375 | 0.39072 | 0.40416 | 0.42809 | 0.46169 | 0.49486 | 0.52779 | 0.56069 | 0.59362 | 0.62663 | 0.65972 | 0.6929 | 0.72618 | 0.73804 | 0.125 | 7 | 723.5367 | 733.6552 | 740.3651 | 747.0377 | 753.6606 | 760.2307 | 766.7704 | 773.3578 | 780.1752 | 787.557 | 795.9185 | 805.2364 | 814.4454 | 823.5194 | 832.4442 | 841.2089 | 849.8132 | 858.2536 | 866.5329 | 874.6485 | 880.3627
7.1 | 0.33972 | 0.30785 | 0.30891 | 0.31046 | 0.31242 | 0.31475 | 0.31745 | 0.32079 | 0.32558 | 0.3336 | 0.3478 | 0.37225 | 0.40668 | 0.44105 | 0.47545 | 0.50993 | 0.54447 | 0.57911 | 0.61382 | 0.64866 | 0.66293 | 0.1125 | 7.1 | 723.5367 | 733.583 | 740.2449 | 746.8768 | 753.465 | 759.9983 | 766.4735 | 772.9135 | 779.3963 | 786.1039 | 793.4054 | 801.7112 | 810.9415 | 820.0221 | 828.9418 | 837.7006 | 846.295 | 854.7278 | 862.9957 | 871.1013 | 876.8892
7.2 | 0.27541 | 0.2439 | 0.24517 | 0.24704 | 0.24944 | 0.25232 | 0.2556 | 0.25931 | 0.2637 | 0.26925 | 0.2778 | 0.29282 | 0.3185 | 0.35439 | 0.39034 | 0.42636 | 0.46246 | 0.49864 | 0.53492 | 0.57132 | 0.58804 | 0.1 | 7.2 | 723.5367 | 733.4924 | 740.0943 | 746.6723 | 753.2145 | 759.708 | 766.1416 | 772.5124 | 778.8428 | 785.2458 | 791.898 | 799.1123 | 807.2899 | 816.3661 | 825.2808 | 834.0304 | 842.6178 | 851.0399 | 859.2985 | 867.3898 | 873.2536
7.3 | 0.21174 | 0.18063 | 0.18205 | 0.18418 | 0.18695 | 0.19032 | 0.1942 | 0.19853 | 0.203 | 0.20793 | 0.21431 | 0.22408 | 0.24057 | 0.26783 | 0.30534 | 0.34292 | 0.38057 | 0.41832 | 0.45618 | 0.49418 | 0.51342 | 0.0875 | 7.3 | 723.5367 | 733.3877 | 739.9195 | 746.4321 | 752.9153 | 759.358 | 765.747 | 772.0711 | 778.3622 | 784.6375 | 790.9536 | 797.478 | 804.5386 | 812.5505 | 821.4567 | 830.2001 | 838.7776 | 847.191 | 855.4362 | 863.5142 | 869.4522
7.4 | 0.14879 | 0.11809 | 0.11965 | 0.12199 | 0.12507 | 0.12885 | 0.13327 | 0.13792 | 0.14278 | 0.14808 | 0.15423 | 0.16208 | 0.17344 | 0.19155 | 0.22044 | 0.25959 | 0.29883 | 0.33816 | 0.37763 | 0.41726 | 0.43907 | 0.075 | 7.4 | 723.5367 | 733.2715 | 739.7253 | 746.1627 | 752.5757 | 758.9544 | 765.2876 | 771.5969 | 777.866 | 784.0703 | 790.218 | 796.3807 | 802.7397 | 809.6307 | 817.4716 | 826.2058 | 834.7754 | 843.1762 | 851.4088 | 859.4686 | 865.4833
7.5 | 0.086617 | 0.056362 | 0.058041 | 0.060557 | 0.063898 | 0.06803 | 0.072577 | 0.077523 | 0.083003 | 0.08909 | 0.095868 | 0.1036 | 0.11308 | 0.12607 | 0.14583 | 0.17638 | 0.21721 | 0.25817 | 0.29928 | 0.34057 | 0.36501 | 0.0625 | 7.5 | 723.5367 | 733.1457 | 739.5145 | 745.8689 | 752.2018 | 758.5054 | 764.8044 | 771.0825 | 777.3052 | 783.4466 | 789.4976 | 795.4802 | 801.4735 | 807.6619 | 814.3812 | 822.0485 | 830.6062 | 838.9952 | 847.2104 | 855.2523 | 861.3421
7.6 | 0.025278 | -0.0045086 | -0.0027264 | -4.4003e-05 | 0.0035243 | 0.0076308 | 0.012292 | 0.017673 | 0.023846 | 0.030799 | 0.038472 | 0.046878 | 0.05625 | 0.067376 | 0.082032 | 0.10348 | 0.13576 | 0.17836 | 0.22114 | 0.26412 | 0.29128 | 0.05 | 7.6 | 723.5367 | 733.0112 | 739.2892 | 745.5536 | 751.7986 | 758.0519 | 764.3004 | 770.5128 | 776.6633 | 782.7326 | 788.709 | 794.5907 | 800.4028 | 806.2246 | 812.2397 | 818.7827 | 826.2697 | 834.6421 | 842.8403 | 850.8588 | 857.0264
7.7 | -0.035176 | -0.064475 | -0.062591 | -0.059757 | -0.056309 | -0.052211 | -0.04727 | -0.041382 | -0.034527 | -0.026767 | -0.018186 | -0.0088737 | 0.0011792 | 0.012216 | 0.025034 | 0.041418 | 0.064641 | 0.098742 | 0.14323 | 0.18795 | 0.21788 | 0.0375 | 7.7 | 723.5367 | 732.8689 | 739.0503 | 745.219 | 751.4038 | 757.5937 | 763.7603 | 769.8812 | 775.9403 | 781.9257 | 787.8258 | 793.6317 | 799.342 | 804.9809 | 810.6267 | 816.4617 | 822.8197 | 830.1161 | 838.2918 | 846.287 | 852.5308
7.8 | -0.094701 | -0.12348 | -0.1215 | -0.11885 | -0.11549 | -0.11121 | -0.10588 | -0.099469 | -0.091994 | -0.083512 | -0.074112 | -0.063883 | -0.052905 | -0.04116 | -0.028393 | -0.013798 | 0.0044152 | 0.029523 | 0.06557 | 0.11206 | 0.14486 | 0.025 | 7.8 | 723.5367 | 732.7187 | 738.7986 | 744.9005 | 751.014 | 757.1121 | 763.1745 | 769.1878 | 775.1436 | 781.0335 | 786.8484 | 792.5771 | 798.2099 | 803.7442 | 809.2031 | 814.6641 | 820.3088 | 826.4703 | 833.5639 | 841.5299 | 847.8526
7.9 | -0.15324 | -0.18149 | -0.17974 | -0.17723 | -0.17375 | -0.16916 | -0.1634 | -0.15649 | -0.14845 | -0.13934 | -0.12921 | -0.11814 | -0.10622 | -0.093513 | -0.07999 | -0.065394 | -0.048912 | -0.02875 | -0.0016306 | 0.036494 | 0.07222 | 0.0125 | 7.9 | 723.5367 | 732.5611 | 738.5688 | 744.5937 | 750.6089 | 756.5949 | 762.5397 | 768.437 | 774.281 | 780.0664 | 785.7848 | 791.4267 | 796.9793 | 802.4321 | 807.7817 | 813.0504 | 818.315 | 823.7571 | 829.7091 | 836.5863 | 842.9863
8 | -0.21074 | -0.23876 | -0.2372 | -0.23462 | -0.23089 | -0.22593 | -0.21975 | -0.21237 | -0.20382 | -0.19414 | -0.18336 | -0.17154 | -0.15874 | -0.14505 | -0.13051 | -0.1151 | -0.098557 | -0.080063 | -0.057822 | -0.028554 | 0 | 0 | 8 | 723.5367 | 732.4305 | 738.3561 | 744.2773 | 750.1746 | 756.0365 | 761.8574 | 767.633 | 773.3598 | 779.0325 | 784.6447 | 790.1871 | 795.649 | 801.0169 | 806.2794 | 811.4326 | 816.4987 | 821.554 | 826.7798 | 832.5084 | 837.9289
8.1 | -0.26749 | -0.29521 | -0.29363 | -0.29084 | -0.28679 | -0.28147 | -0.27489 | -0.26707 | -0.25805 | -0.24784 | -0.23646 | -0.22395 | -0.21035 | -0.19573 | -0.18015 | -0.16367 | -0.14625 | -0.12763 | -0.10698 | -0.082524 | 0 | 0 | 8.1 | 723.5367 | 732.322 | 738.1388 | 743.937 | 749.705 | 755.4373 | 761.1299 | 766.7804 | 772.3846 | 777.9383 | 783.4349 | 788.8672 | 794.2248 | 799.4964 | 804.668 | 809.7279 | 814.6717 | 819.5215 | 824.3534 | 829.3483 | 833.7342
8.2 | -0.32355 | -0.35073 | -0.34883 | -0.34578 | -0.34141 | -0.33573 | -0.32877 | -0.32055 | -0.31107 | -0.30035 | -0.28841 | -0.27526 | -0.26093 | -0.24545 | -0.22888 | -0.21129 | -0.19273 | -0.17316 | -0.15232 | -0.098599 | 0 | 0 | 8.2 | 723.5367 | 732.1966 | 737.9028 | 743.5666 | 749.1998 | 754.7986 | 760.3604 | 765.8817 | 771.3591 | 776.7873 | 782.1611 | 787.4729 | 792.7149 | 797.8762 | 802.9451 | 807.9073 | 812.7509 | 817.4713 | 822.0902 | 823.4819 | 827.251
8.3 | -0.37871 | -0.4052 | -0.40286 | -0.39937 | -0.3947 | -0.38869 | -0.38137 | -0.37275 | -0.36284 | -0.35163 | -0.33914 | -0.32538 | -0.31034 | -0.29407 | -0.27658 | -0.25793 | -0.2382 | -0.21742 | -0.16477 | -0.10097 | 0 | 0 | 8.3 | 723.5367 | 732.0341 | 737.6243 | 743.1657 | 748.6604 | 754.1232 | 759.5507 | 764.9394 | 770.2848 | 775.5822 | 780.8256 | 786.0091 | 791.1246 | 796.1639 | 801.1159 | 805.9685 | 810.7072 | 815.3199 | 816.6002 | 816.7516 | 820.2405
8.4 | -0.43273 | -0.45844 | -0.45572 | -0.45175 | -0.44663 | -0.44032 | -0.43265 | -0.42364 | -0.41329 | -0.40161 | -0.38858 | -0.37421 | -0.3585 | -0.34145 | -0.3231 | -0.30347 | -0.28261 | -0.2298 | -0.16606 | -0.099884 | 0 | 0 | 8.4 | 723.5367 | 731.8357 | 737.2969 | 742.7182 | 748.0893 | 753.4127 | 758.7025 | 763.954 | 769.1629 | 774.3235 | 779.4307 | 784.4779 | 789.4587 | 794.3648 | 799.1878 | 803.9162 | 808.538 | 809.8366 | 809.9819 | 809.8542 | 813.2468
8.5 | -0.48537 | -0.51028 | -0.5073 | -0.50295 | -0.49734 | -0.49056 | -0.48256 | -0.47317 | -0.46239 | -0.45022 | -0.43665 | -0.42168 | -0.4053 | -0.38752 | -0.36833 | -0.34777 | -0.29506 | -0.23125 | -0.16491 | -0.098724 | 0 | 0 | 8.5 | 723.5367 | 731.6121 | 736.9294 | 742.2207 | 747.4708 | 752.6689 | 757.8164 | 762.9264 | 767.9932 | 773.0119 | 777.9762 | 782.8808 | 787.7186 | 792.4831 | 797.1658 | 801.7579 | 803.0464 | 803.2009 | 803.0915 | 802.9811 | 806.3577
8.6 | -0.53651 | -0.56059 | -0.55748 | -0.55286 | -0.54685 | -0.53956 | -0.53105 | -0.52128 | -0.51006 | -0.4974 | -0.48329 | -0.46771 | -0.45067 | -0.43215 | -0.41216 | -0.35991 | -0.29639 | -0.23017 | -0.16391 | -0.098152 | 0 | 0 | 8.6 | 723.5367 | 731.3733 | 736.5358 | 741.6823 | 746.8006 | 751.8749 | 756.8933 | 761.8562 | 766.776 | 771.6466 | 776.4627 | 781.2177 | 785.906 | 790.5203 | 795.054 | 796.297 | 796.422 | 796.3026 | 796.2013 | 796.1515 | 799.537
8.7 | -0.58606 | -0.60932 | -0.60612 | -0.60134 | -0.59505 | -0.58731 | -0.57825 | -0.56792 | -0.55626 | -0.54311 | -0.52844 | -0.51226 | -0.49455 | -0.4753 | -0.42371 | -0.36078 | -0.29501 | -0.22906 | -0.16341 | -0.097988 | 0 | 0 | 8.7 | 723.5367 | 731.1263 | 736.1259 | 741.116 | 746.0868 | 751.0254 | 755.9151 | 760.7434 | 765.5102 | 770.2275 | 774.8888 | 779.4887 | 784.0203 | 788.4777 | 789.6527 | 789.7196 | 789.5548 | 789.4241 | 789.3639 | 789.3478 | 792.7415
8.8 | -0.63397 | -0.65641 | -0.65315 | -0.64827 | -0.64177 | -0.6337 | -0.62415 | -0.6132 | -0.60094 | -0.58728 | -0.57205 | -0.55525 | -0.53686 | -0.48609 | -0.4239 | -0.35881 | -0.29344 | -0.22826 | -0.16314 | -0.097941 | 0 | 0 | 8.8 | 723.5367 | 730.8743 | 735.7064 | 740.5308 | 745.3413 | 750.1276 | 754.8762 | 759.5698 | 764.1957 | 768.7532 | 773.2544 | 777.6924 | 782.0614 | 783.1541 | 783.1451 | 782.9126 | 782.7239 | 782.618 | 782.572 | 782.5572 | 785.9505
8.9 | -0.68023 | -0.70184 | -0.69852 | -0.69354 | -0.68689 | -0.67857 | -0.66863 | -0.65713 | -0.64419 | -0.62985 | -0.61405 | -0.59662 | -0.54677 | -0.48545 | -0.42118 | -0.35657 | -0.29206 | -0.22752 | -0.16279 | -0.097807 | 0 | 0 | 8.9 | 723.5367 | 730.6188 | 735.279 | 739.932 | 744.5721 | 749.1926 | 753.783 | 758.3292 | 762.8138 | 767.2235 | 771.5578 | 775.8282 | 776.8277 | 776.7309 | 776.4164 | 776.1522 | 775.9782 | 775.8737 | 775.8127 | 775.7801 | 779.1621
9 | -0.7248 | -0.74556 | -0.74218 | -0.7371 | -0.73031 | -0.72177 | -0.71152 | -0.69957 | -0.68602 | -0.67093 | -0.65439 | -0.60555 | -0.5452 | -0.48185 | -0.41812 | -0.35444 | -0.29065 | -0.2266 | -0.1622 | -0.097494 | 0 | 0 | 9 | 723.5367 | 730.3589 | 734.8443 | 739.3208 | 743.784 | 748.2282 | 752.6464 | 757.0278 | 761.358 | 765.6193 | 769.7984 | 770.6948 | 770.4999 | 770.0929 | 769.7411 | 769.4849 | 769.3043 | 769.1748 | 769.0832 | 769.0243 | 772.3864
9.1 | -0.76766 | -0.78755 | -0.7841 | -0.77891 | -0.77195 | -0.76322 | -0.75269 | -0.74037 | -0.72629 | -0.71052 | -0.6624 | -0.60295 | -0.54063 | -0.47787 | -0.41511 | -0.35221 | -0.28897 | -0.22533 | -0.1613 | -0.096975 | 0 | 0 | 9.1 | 723.5367 | 730.0942 | 734.4005 | 738.6967 | 742.9775 | 747.2386 | 751.4738 | 755.6762 | 759.8344 | 763.9341 | 764.7582 | 764.4727 | 763.9631 | 763.5137 | 763.1646 | 762.8961 | 762.6838 | 762.5156 | 762.3878 | 762.3025 | 765.6369
9.2 | -0.80877 | -0.82776 | -0.82423 | -0.81891 | -0.81179 | -0.80283 | -0.79203 | -0.77936 | -0.76484 | -0.71773 | -0.65907 | -0.59747 | -0.53562 | -0.47389 | -0.41196 | -0.34965 | -0.28689 | -0.22368 | -0.16011 | -0.096269 | 0 | 0 | 9.2 | 723.5367 | 729.8231 | 733.9465 | 738.0577 | 742.152 | 746.224 | 750.2693 | 754.2816 | 758.2536 | 758.9752 | 758.6111 | 758.0299 | 757.4904 | 757.0386 | 756.672 | 756.3663 | 756.1097 | 755.8986 | 755.7363 | 755.6265 | 758.9281
9.3 | -0.8481 | -0.86616 | -0.86253 | -0.85706 | -0.84975 | -0.84056 | -0.82947 | -0.81647 | -0.77078 | -0.71337 | -0.6528 | -0.59174 | -0.53074 | -0.46972 | -0.40844 | -0.34664 | -0.28437 | -0.22167 | -0.15865 | -0.095396 | 0 | 0 | 9.3 | 723.5367 | 729.545 | 733.4802 | 737.4023 | 741.305 | 745.1837 | 749.0329 | 752.8479 | 753.4244 | 752.9334 | 752.2505 | 751.6331 | 751.1095 | 750.6525 | 750.2436 | 749.8884 | 749.5834 | 749.3321 | 749.1386 | 749.0085 | 752.2725
9.4 | -0.88558 | -0.90269 | -0.89895 | -0.89332 | -0.8858 | -0.87635 | -0.86496 | -0.82086 | -0.76498 | -0.70584 | -0.64604 | -0.58607 | -0.52584 | -0.46529 | -0.40441 | -0.34315 | -0.28143 | -0.21934 | -0.15696 | -0.094387 | 0 | 0 | 9.4 | 723.5367 | 729.2587 | 733.0008 | 736.7282 | 740.4348 | 744.1149 | 747.7634 | 748.1776 | 747.5307 | 746.7036 | 745.9601 | 745.3347 | 744.7993 | 744.3182 | 743.872 | 743.4634 | 743.1131 | 742.8252 | 742.6056 | 742.4578 | 745.6811
9.5 | -0.92117 | -0.9373 | -0.93344 | -0.92765 | -0.91989 | -0.91016 | -0.86771 | -0.81345 | -0.75591 | -0.69766 | -0.63912 | -0.58015 | -0.52062 | -0.46053 | -0.40001 | -0.3392 | -0.27813 | -0.21672 | -0.15508 | -0.093261 | 0 | 0 | 9.5 | 723.5367 | 728.9639 | 732.5066 | 736.034 | 739.5389 | 743.0156 | 743.2616 | 742.4493 | 741.4609 | 740.5623 | 739.7927 | 739.1307 | 738.5474 | 738.0224 | 737.5411 | 737.0994 | 736.7074 | 736.3883 | 736.1456 | 735.9834 | 739.1624
9.6 | -0.95482 | -0.96993 | -0.96595 | -0.95997 | -0.95197 | -0.91122 | -0.85863 | -0.80275 | -0.74613 | -0.6892 | -0.63177 | -0.57368 | -0.51485 | -0.45535 | -0.39533 | -0.33499 | -0.27449 | -0.21387 | -0.15303 | -0.092039 | 0 | 0 | 9.6 | 723.5367 | 728.6596 | 731.9971 | 735.318 | 738.6157 | 738.6875 | 737.7046 | 736.5491 | 735.486 | 734.5552 | 733.7378 | 733.0097 | 732.3579 | 731.7738 | 731.2528 | 730.7877 | 730.3768 | 730.0295 | 729.7673 | 729.5919 | 732.7245
9.7 | -0.98645 | -1.0005 | -0.99641 | -0.99024 | -0.95127 | -0.90043 | -0.84626 | -0.79133 | -0.73605 | -0.68026 | -0.62377 | -0.56648 | -0.50841 | -0.44965 | -0.39033 | -0.33063 | -0.27074 | -0.2108 | -0.15083 | -0.090728 | 0 | 0 | 9.7 | 723.5367 | 728.3458 | 731.4711 | 734.5796 | 734.4686 | 733.3078 | 731.9793 | 730.7467 | 729.6487 | 728.6666 | 727.7769 | 726.9692 | 726.24 | 725.5917 | 725.0235 | 724.5328 | 724.1119 | 723.7575 | 723.4769 | 723.2903 | 726.3733
9.8 | -1.016 | -1.029 | -1.0248 | -0.98769 | -0.93868 | -0.88631 | -0.83313 | -0.77957 | -0.72546 | -0.67063 | -0.61497 | -0.5585 | -0.50128 | -0.4434 | -0.38495 | -0.32608 | -0.26694 | -0.2077 | -0.1485 | -0.089338 | 0 | 0 | 9.8 | 723.5367 | 728.0215 | 730.9283 | 730.6233 | 729.2748 | 727.7647 | 726.3554 | 725.0845 | 723.9325 | 722.8753 | 721.9025 | 721.0114 | 720.2068 | 719.4931 | 718.8747 | 718.3502 | 717.9156 | 717.561 | 717.2816 | 717.0836 | 720.1151
9.9 | -1.0434 | -1.0553 | -1.0202 | -0.97319 | -0.92272 | -0.8714 | -0.81964 | -0.76728 | -0.71416 | -0.66019 | -0.60538 | -0.54978 | -0.4935 | -0.43659 | -0.37915 | -0.32127 | -0.26305 | -0.20464 | -0.14621 | -0.08787 | 0 | 0 | 9.9 | 723.5367 | 727.687 | 727.1748 | 725.6265 | 723.9238 | 722.3278 | 720.8755 | 719.5466 | 718.3162 | 717.1732 | 716.1142 | 715.1442 | 714.2681 | 713.4931 | 712.8227 | 712.2599 | 711.8013 | 711.4413 | 711.1688 | 710.978 | 713.9548
10 | -1.0687 | -1.0487 | -1.0037 | -0.95528 | -0.90592 | -0.85607 | -0.80556 | -0.75424 | -0.70201 | -0.64892 | -0.59501 | -0.54038 | -0.4851 | -0.42926 | -0.37291 | -0.31613 | -0.25898 | -0.20156 | -0.14401 | -0.086496 | 0 | 0 | 10 | 723.5367 | 724.1495 | 722.3875 | 720.4796 | 718.6851 | 717.0403 | 715.5246 | 714.1124 | 712.7922 | 711.5597 | 710.4192 | 709.3749 | 708.434 | 707.6009 | 706.8811 | 706.2762 | 705.7875 | 705.4106 | 705.1388 | 704.9607 | 707.8983
10.1 | -1.061 | -1.03 | -0.98374 | -0.93647 | -0.88864 | -0.8401 | -0.79068 | -0.74031 | -0.689 | -0.63684 | -0.58393 | -0.53033 | -0.47614 | -0.42143 | -0.36624 | -0.31062 | -0.25464 | -0.19835 | -0.14185 | -0.085271 | 0 | 0 | 10.1 | 723.5367 | 719.5854 | 717.4579 | 715.4516 | 713.6018 | 711.8874 | 710.2826 | 708.7752 | 707.3607 | 706.0426 | 704.8245 | 703.7128 | 702.7112 | 701.8251 | 701.0571 | 700.411 | 699.8874 | 699.4866 | 699.2036 | 699.0316 | 701.9328
10.2 | -1.0258 | -0.99249 | -0.96279 | -0.91712 | -0.87067 | -0.82328 | -0.77486 | -0.72546 | -0.67515 | -0.62403 | -0.57218 | -0.5197 | -0.46666 | -0.41313 | -0.35914 | -0.30475 | -0.25 | -0.19493 | -0.13961 | -0.084043 | 0 | 0 | 10.2 | 723.5367 | 716.4827 | 712.6545 | 710.5859 | 708.6596 | 706.8494 | 705.1432 | 703.5357 | 702.0302 | 700.6298 | 699.3403 | 698.1645 | 697.1073 | 696.1704 | 695.3577 | 694.6705 | 694.1119 | 693.6818 | 693.3804 | 693.1937 | 696.0491
10.3 | -0.97463 | -0.94139 | -0.9259 | -0.89701 | -0.85178 | -0.80545 | -0.75807 | -0.70972 | -0.6605 | -0.61049 | -0.55981 | -0.50852 | -0.45669 | -0.40439 | -0.35165 | -0.29852 | -0.24505 | -0.19126 | -0.13713 | -0.082632 | 0 | 0 | 10.3 | 723.5367 | 714.8178 | 709.6159 | 705.868 | 703.8388 | 701.9204 | 700.1075 | 698.4029 | 696.8092 | 695.3321 | 693.9737 | 692.7383 | 691.6269 | 690.6427 | 689.7863 | 689.0608 | 688.4667 | 688.0071 | 687.6729 | 687.4568 | 690.2522
10.4 | -0.91554 | -0.88278 | -0.87566 | -0.86058 | -0.83181 | -0.78659 | -0.74032 | -0.69312 | -0.64508 | -0.59629 | -0.54684 | -0.49681 | -0.44625 | -0.39522 | -0.34377 | -0.29195 | -0.23979 | -0.18725 | -0.13429 | -0.080961 | 0 | 0 | 10.4 | 723.5367 | 714.0429 | 708.0358 | 702.8736 | 699.1339 | 697.1017 | 695.1849 | 693.3855 | 691.7089 | 690.1571 | 688.7338 | 687.4395 | 686.2768 | 685.2456 | 684.3482 | 683.5846 | 682.9577 | 682.4591 | 682.0846 | 681.8336 | 684.5587
10.5 | -0.85302 | -0.82057 | -0.81752 | -0.81049 | -0.79543 | -0.76671 | -0.72166 | -0.6757 | -0.62893 | -0.58144 | -0.5333 | -0.48458 | -0.43535 | -0.38564 | -0.33553 | -0.28504 | -0.23415 | -0.18282 | -0.13108 | -0.079036 | 0 | 0 | 10.5 | 723.5367 | 713.7132 | 707.3042 | 701.3055 | 696.141 | 692.403 | 690.3843 | 688.4952 | 686.7374 | 685.1145 | 683.6264 | 682.2756 | 681.0612 | 679.985 | 679.0462 | 678.2471 | 677.5787 | 677.0364 | 676.6208 | 676.3403 | 678.9871
10.6 | -0.78914 | -0.75679 | -0.75547 | -0.7524 | -0.74542 | -0.73051 | -0.7021 | -0.65748 | -0.61207 | -0.56595 | -0.51919 | -0.47185 | -0.42398 | -0.37566 | -0.32691 | -0.27773 | -0.22807 | -0.17799 | -0.12757 | -0.076916 | 0 | 0 | 10.6 | 723.5367 | 713.5747 | 706.9851 | 700.574 | 694.578 | 689.4276 | 685.7177 | 683.7403 | 681.9046 | 680.2104 | 678.6597 | 677.2512 | 675.9865 | 674.8643 | 673.886 | 673.0421 | 672.3274 | 671.7415 | 671.293 | 670.9892 | 673.5548
10.7 | -0.7247 | -0.69235 | -0.69174 | -0.69044 | -0.68753 | -0.68083 | -0.66636 | -0.63849 | -0.59452 | -0.54983 | -0.50451 | -0.45859 | -0.41216 | -0.36526 | -0.31787 | -0.26995 | -0.22157 | -0.17282 | -0.12382 | -0.074655 | 0 | 0 | 10.7 | 723.5367 | 713.5105 | 706.846 | 700.259 | 693.8629 | 687.8958 | 682.7873 | 679.131 | 677.217 | 675.4533 | 673.8384 | 672.3735 | 671.057 | 669.89 | 668.8623 | 667.9681 | 667.2065 | 666.5852 | 666.1108 | 665.792 | 668.2733
10.8 | -0.66001 | -0.62766 | -0.62739 | -0.62691 | -0.6259 | -0.62341 | -0.61725 | -0.60341 | -0.57626 | -0.53308 | -0.48925 | -0.44483 | -0.39988 | -0.35438 | -0.3083 | -0.26171 | -0.21471 | -0.16741 | -0.11992 | -0.072306 | 0 | 0 | 10.8 | 723.5367 | 713.4776 | 706.7854 | 700.1355 | 693.5779 | 687.2247 | 681.3119 | 676.2673 | 672.6831 | 670.8482 | 669.1702 | 667.647 | 666.2795 | 665.0573 | 663.974 | 663.0284 | 662.2273 | 661.5769 | 661.085 | 660.7548 | 663.1515
10.9 | -0.59521 | -0.5629 | -0.56289 | -0.5629 | -0.56284 | -0.56236 | -0.56049 | -0.55505 | -0.54199 | -0.51569 | -0.47342 | -0.43055 | -0.38706 | -0.34293 | -0.29823 | -0.25306 | -0.20755 | -0.1618 | -0.11589 | -0.069891 | 0 | 0 | 10.9 | 723.5367 | 713.4649 | 706.7679 | 700.1046 | 693.4979 | 686.9951 | 680.7065 | 674.8665 | 669.9015 | 666.4031 | 664.6597 | 663.0788 | 661.6497 | 660.3657 | 659.2252 | 658.2349 | 657.4001 | 656.7282 | 656.2216 | 655.8841 | 658.1941
11 | -0.53042 | -0.49821 | -0.49846 | -0.49886 | -0.4994 | -0.49997 | -0.50019 | -0.4991 | -0.4945 | -0.48234 | -0.457 | -0.41565 | -0.3736 | -0.33091 | -0.28769 | -0.24407 | -0.20016 | -0.15604 | -0.11178 | -0.067429 | 0 | 0 | 11 | 723.5367 | 713.4719 | 706.7848 | 700.1304 | 693.522 | 686.9802 | 680.5507 | 674.3424 | 668.5887 | 663.7155 | 660.3144 | 658.6648 | 657.1673 | 655.8196 | 654.6283 | 653.5985 | 652.737 | 652.0458 | 651.528 | 651.1828 | 653.4056
11.1 | -0.46576 | -0.43372 | -0.43423 | -0.435 | -0.43603 | -0.43727 | -0.43861 | -0.43967 | -0.43948 | -0.43582 | -0.42459 | -0.40006 | -0.35952 | -0.31837 | -0.27676 | -0.23479 | -0.19257 | -0.15014 | -0.10758 | -0.064914 | 0 | 0 | 11.1 | 723.5367 | 713.4993 | 706.8349 | 700.2022 | 693.6127 | 687.0777 | 680.6164 | 674.2737 | 668.1578 | 662.5019 | 657.7229 | 654.4052 | 652.8369 | 651.4318 | 650.1945 | 649.1319 | 648.2454 | 647.5378 | 647.0076 | 646.6558 | 648.7887
11.2 | -0.40135 | -0.36956 | -0.37031 | -0.37143 | -0.37291 | -0.37471 | -0.37678 | -0.37902 | -0.38103 | -0.38174 | -0.3789 | -0.36846 | -0.34484 | -0.30537 | -0.26548 | -0.22526 | -0.18478 | -0.1441 | -0.10328 | -0.062349 | 0 | 0 | 11.2 | 723.5367 | 713.5468 | 706.9172 | 700.3172 | 693.7579 | 687.2489 | 680.8008 | 674.4321 | 668.1875 | 662.1664 | 656.5943 | 651.8969 | 648.6716 | 647.2136 | 645.9368 | 644.8427 | 643.9338 | 643.208 | 642.6662 | 642.3056 | 644.3475
11.3 | -0.33732 | -0.30582 | -0.30679 | -0.30824 | -0.31014 | -0.31245 | -0.31514 | -0.31816 | -0.32131 | -0.32413 | -0.32563 | -0.32369 | -0.31433 | -0.29195 | -0.25387 | -0.21546 | -0.1768 | -0.13792 | -0.098879 | -0.059721 | 0 | 0 | 11.3 | 723.5367 | 713.613 | 707.0296 | 700.4728 | 693.9534 | 687.4809 | 681.0645 | 674.7146 | 668.4408 | 662.2805 | 656.3413 | 650.8622 | 646.2752 | 643.1783 | 641.8632 | 640.74 | 639.8064 | 639.0629 | 638.5066 | 638.1377 | 640.0852
11.4 | -0.27379 | -0.24262 | -0.24378 | -0.24553 | -0.24781 | -0.2506 | -0.25386 | -0.25746 | -0.26129 | -0.26522 | -0.26894 | -0.27151 | -0.27081 | -0.26283 | -0.24194 | -0.20541 | -0.16861 | -0.13158 | -0.094363 | -0.057028 | 0 | 0 | 11.4 | 723.5367 | 713.6959 | 707.169 | 700.6656 | 694.1957 | 687.7689 | 681.3947 | 675.0732 | 668.8075 | 662.6159 | 656.5487 | 650.7204 | 645.37 | 640.9261 | 637.9828 | 636.828 | 635.8701 | 635.1057 | 634.535 | 634.1554 | 636.0067
11.5 | -0.21084 | -0.18004 | -0.18138 | -0.18338 | -0.18601 | -0.18924 | -0.19294 | -0.19701 | -0.2014 | -0.20612 | -0.21112 | -0.21608 | -0.22003 | -0.22081 | -0.21438 | -0.19509 | -0.16019 | -0.12505 | -0.089725 | -0.054256 | 0 | 0 | 11.5 | 723.5367 | 713.7931 | 707.3322 | 700.8919 | 694.4811 | 688.1094 | 681.7775 | 675.4875 | 669.2482 | 663.0757 | 656.9951 | 651.0569 | 645.3721 | 640.1754 | 635.892 | 633.1139 | 632.1281 | 631.3428 | 630.755 | 630.3651 | 632.1163
11.6 | -0.14856 | -0.11816 | -0.11965 | -0.12187 | -0.12482 | -0.12837 | -0.1324 | -0.13689 | -0.14185 | -0.14731 | -0.15328 | -0.15966 | -0.16609 | -0.17159 | -0.17397 | -0.16917 | -0.15154 | -0.11835 | -0.084948 | -0.051407 | 0 | 0 | 11.6 | 723.5367 | 713.9028 | 707.5162 | 701.1477 | 694.8055 | 688.4896 | 682.2021 | 675.9524 | 669.7555 | 663.6273 | 657.5838 | 651.6468 | 645.8624 | 640.3384 | 635.3072 | 631.1929 | 628.5875 | 627.778 | 627.1734 | 626.771 | 628.4201
11.7 | -0.087021 | -0.057052 | -0.058671 | -0.061101 | -0.064241 | -0.067994 | -0.072331 | -0.077264 | -0.082821 | -0.089019 | -0.095857 | -0.1033 | -0.11123 | -0.11925 | -0.12638 | -0.13042 | -0.12732 | -0.11143 | -0.080029 | -0.048467 | 0 | 0 | 11.7 | 723.5367 | 714.0234 | 707.7184 | 701.4297 | 695.1561 | 688.8981 | 682.6644 | 676.47 | 670.3313 | 664.2635 | 658.2788 | 652.3893 | 646.6131 | 640.9944 | 635.6397 | 630.7813 | 626.8434 | 624.4186 | 623.7945 | 623.3805 | 624.923
11.8 | -0.026285 | 0.003225 | 0.0014864 | -0.0010436 | -0.0042825 | -0.0082124 | -0.012862 | -0.018265 | -0.024439 | -0.031376 | -0.039053 | -0.047437 | -0.056473 | -0.066027 | -0.075715 | -0.084543 | -0.090322 | -0.089007 | -0.074954 | -0.04544 | 0 | 0 | 11.8 | 723.5367 | 714.1538 | 707.9371 | 701.7268 | 695.5223 | 689.3308 | 683.166 | 677.0432 | 670.9779 | 664.9827 | 659.0688 | 653.245 | 647.5211 | 641.9143 | 636.4685 | 631.2904 | 626.6127 | 622.8602 | 620.626 | 620.1982 | 621.6321
11.9 | 0.033591 | 0.062617 | 0.06085 | 0.058302 | 0.054982 | 0.050847 | 0.04585 | 0.03996 | 0.033177 | 0.025523 | 0.017039 | 0.0077689 | -0.0022428 | -0.012942 | -0.024193 | -0.035619 | -0.046232 | -0.053845 | -0.054419 | -0.042313 | 0 | 0 | 11.9 | 723.5367 | 714.2931 | 708.1622 | 702.0296 | 695.9015 | 689.7901 | 683.7096 | 677.6738 | 671.6946 | 665.7832 | 659.9488 | 654.2006 | 648.5461 | 642.9952 | 637.565 | 632.3 | 627.3074 | 622.8204 | 619.2642 | 617.2324 | 618.5528
12 | 0.092554 | 0.12115 | 0.11943 | 0.11687 | 0.11343 | 0.10904 | 0.10367 | 0.097291 | 0.089921 | 0.081591 | 0.072344 | 0.062232 | 0.051299 | 0.039589 | 0.027151 | 0.014115 | 0.00085489 | -0.011646 | -0.021206 | -0.023788 | 0 | 0 | 12 | 723.5367 | 714.4324 | 708.3857 | 702.3369 | 696.2974 | 690.2803 | 684.2979 | 678.361 | 672.479 | 666.6607 | 660.9149 | 655.2499 | 649.6746 | 644.1967 | 638.8265 | 633.5819 | 628.5077 | 623.7115 | 619.4269 | 616.0794 | 615.6928
12.1 | 0.15063 | 0.17884 | 0.17717 | 0.17455 | 0.17093 | 0.16625 | 0.16048 | 0.15362 | 0.1457 | 0.13674 | 0.12678 | 0.11587 | 0.10406 | 0.09139 | 0.077896 | 0.063624 | 0.0487 | 0.033493 | 0.018985 | 0.0073537 | 0 | 0 | 12.1 | 723.5367 | 714.5639 | 708.6071 | 702.6535 | 696.7157 | 690.8052 | 684.9316 | 679.1032 | 673.327 | 667.6107 | 661.9617 | 656.3888 | 650.9005 | 645.506 | 640.2136 | 635.0342 | 629.9859 | 625.1142 | 620.5267 | 616.4574 | 614.6495
12.2 | 0.20787 | 0.23568 | 0.23395 | 0.23121 | 0.22736 | 0.22235 | 0.21619 | 0.20888 | 0.20043 | 0.19088 | 0.18026 | 0.1686 | 0.15596 | 0.14237 | 0.12786 | 0.11248 | 0.096261 | 0.07933 | 0.062052 | 0.037755 | 0 | 0 | 12.2 | 723.5367 | 714.6921 | 708.8318 | 702.9858 | 697.1612 | 691.3669 | 685.6104 | 679.8976 | 674.2348 | 668.628 | 663.0846 | 657.6122 | 652.2201 | 646.9173 | 641.7136 | 636.6176 | 631.6406 | 626.8011 | 622.1447 | 618.575 | 615.9357
12.3 | 0.26428 | 0.2916 | 0.28971 | 0.28675 | 0.28263 | 0.27729 | 0.27074 | 0.26299 | 0.25405 | 0.24394 | 0.2327 | 0.22034 | 0.2069 | 0.19242 | 0.17694 | 0.16049 | 0.1431 | 0.12482 | 0.098098 | 0.060882 | 0 | 0 | 12.3 | 723.5367 | 714.8281 | 709.0709 | 703.3395 | 697.637 | 691.9662 | 686.3328 | 680.7418 | 675.1984 | 669.7085 | 664.2783 | 658.9157 | 653.6289 | 648.4276 | 643.3212 | 638.3199 | 633.4327 | 628.6711 | 624.8495 | 622.2662 | 619.2182
12.4 | 0.31977 | 0.34651 | 0.34437 | 0.3411 | 0.33666 | 0.331 | 0.32407 | 0.3159 | 0.30649 | 0.29585 | 0.28401 | 0.27098 | 0.25679 | 0.24147 | 0.22504 | 0.20756 | 0.18904 | 0.16187 | 0.12364 | 0.076126 | 0 | 0 | 12.4 | 723.5367 | 714.9817 | 709.3359 | 703.722 | 698.1444 | 692.6027 | 687.0975 | 681.6334 | 676.2153 | 670.8485 | 665.5394 | 660.2947 | 655.1229 | 650.0325 | 645.0337 | 640.1361 | 635.3502 | 631.4809 | 628.7924 | 627.1337 | 623.9073
12.5 | 0.37421 | 0.40029 | 0.39788 | 0.39426 | 0.38945 | 0.38343 | 0.37614 | 0.36755 | 0.35768 | 0.34653 | 0.33412 | 0.32045 | 0.30553 | 0.2894 | 0.27207 | 0.25358 | 0.22631 | 0.18786 | 0.13989 | 0.085309 | 0 | 0 | 12.5 | 723.5367 | 715.1574 | 709.6329 | 704.1407 | 698.6875 | 693.2755 | 687.9031 | 682.5708 | 677.2832 | 672.0459 | 666.8646 | 661.7463 | 656.698 | 651.7287 | 646.8471 | 642.0637 | 638.1839 | 635.4711 | 633.7648 | 632.7779 | 629.4781
12.6 | 0.42746 | 0.45282 | 0.45016 | 0.44621 | 0.441 | 0.43457 | 0.42688 | 0.4179 | 0.40758 | 0.39593 | 0.38295 | 0.36865 | 0.35304 | 0.33612 | 0.31792 | 0.29082 | 0.25239 | 0.20433 | 0.14952 | 0.090554 | 0 | 0 | 12.6 | 723.5367 | 715.3543 | 709.9624 | 704.5983 | 699.2716 | 693.9876 | 688.7484 | 683.5525 | 678.401 | 673.2989 | 668.2523 | 663.2674 | 658.3515 | 653.5121 | 648.7582 | 644.8944 | 642.1841 | 640.4672 | 639.456 | 638.8941 | 635.563
12.7 | 0.47937 | 0.50397 | 0.50112 | 0.49687 | 0.4913 | 0.48443 | 0.4763 | 0.46688 | 0.45612 | 0.44397 | 0.43044 | 0.41553 | 0.39923 | 0.38155 | 0.35485 | 0.31672 | 0.26883 | 0.21405 | 0.15499 | 0.093476 | 0 | 0 | 12.7 | 723.5367 | 715.5692 | 710.3199 | 705.093 | 699.8982 | 694.7442 | 689.6367 | 684.5782 | 679.5677 | 674.6069 | 669.7011 | 664.857 | 660.0809 | 655.3804 | 651.5588 | 648.8778 | 647.1769 | 646.168 | 645.5958 | 645.283 | 641.9363
12.8 | 0.52984 | 0.55366 | 0.55065 | 0.54617 | 0.54027 | 0.53301 | 0.52441 | 0.5145 | 0.50325 | 0.49061 | 0.47652 | 0.46099 | 0.44401 | 0.41793 | 0.38033 | 0.33285 | 0.27838 | 0.21948 | 0.158 | 0.095087 | 0 | 0 | 12.8 | 723.5367 | 715.7977 | 710.7001 | 705.6195 | 700.5653 | 695.5469 | 690.5735 | 685.6514 | 680.7835 | 675.9694 | 671.2109 | 666.5139 | 661.8852 | 658.1268 | 655.4991 | 653.8401 | 652.8606 | 652.3042 | 651.994 | 651.8237 | 648.4692
12.9 | 0.57879 | 0.6018 | 0.59868 | 0.59402 | 0.58785 | 0.58022 | 0.57118 | 0.56075 | 0.54896 | 0.53578 | 0.52114 | 0.50499 | 0.47968 | 0.44278 | 0.39592 | 0.34198 | 0.28351 | 0.22233 | 0.15958 | 0.095945 | 0 | 0 | 12.9 | 723.5367 | 716.0365 | 711.0975 | 706.172 | 701.2678 | 696.3942 | 691.5611 | 686.7783 | 682.0524 | 677.3869 | 672.7814 | 668.2383 | 664.5589 | 662.0028 | 660.4068 | 659.4803 | 658.9659 | 658.6851 | 658.5311 | 658.4459 | 655.0899
13 | 0.62615 | 0.64834 | 0.64513 | 0.64032 | 0.63393 | 0.62599 | 0.61653 | 0.60561 | 0.59325 | 0.57946 | 0.56421 | 0.5398 | 0.50373 | 0.45765 | 0.40441 | 0.34657 | 0.28592 | 0.2236 | 0.16027 | 0.09633 | 0 | 0 | 13 | 723.5367 | 716.283 | 711.5087 | 706.7455 | 702.0005 | 697.2815 | 692.5984 | 687.9614 | 683.3809 | 678.8637 | 674.4134 | 670.8254 | 668.3546 | 666.8373 | 665.9821 | 665.5305 | 665.303 | 665.1912 | 665.1358 | 665.1066 | 661.7558
13.1 | 0.67189 | 0.69324 | 0.68995 | 0.68501 | 0.67843 | 0.67021 | 0.66039 | 0.649 | 0.63607 | 0.62165 | 0.5981 | 0.56294 | 0.51775 | 0.46536 | 0.4083 | 0.34836 | 0.28667 | 0.22387 | 0.16035 | 0.09638 | 0 | 0 | 13.1 | 723.5367 | 716.536 | 711.9311 | 707.3367 | 702.7586 | 698.2041 | 693.6812 | 689.2002 | 684.7718 | 680.4065 | 676.9065 | 674.5283 | 673.102 | 672.3318 | 671.9587 | 671.8025 | 671.7538 | 671.752 | 671.7654 | 671.7778 | 668.4392
13.2 | 0.71595 | 0.73645 | 0.73308 | 0.72802 | 0.72125 | 0.71279 | 0.70264 | 0.69082 | 0.67737 | 0.65468 | 0.62035 | 0.57603 | 0.52455 | 0.46839 | 0.4093 | 0.34839 | 0.28631 | 0.22342 | 0.15998 | 0.096165 | 0 | 0 | 13.2 | 723.5367 | 716.7948 | 712.3642 | 707.9438 | 703.5397 | 699.1576 | 694.8051 | 690.4906 | 686.2248 | 682.8134 | 680.5198 | 679.1811 | 678.503 | 678.2208 | 678.1495 | 678.1795 | 678.2494 | 678.3263 | 678.3927 | 678.4388 | 675.1191
13.3 | 0.7583 | 0.77793 | 0.77447 | 0.76928 | 0.76234 | 0.75365 | 0.74319 | 0.73098 | 0.7094 | 0.67604 | 0.6326 | 0.58195 | 0.52667 | 0.46849 | 0.40849 | 0.34725 | 0.28515 | 0.22242 | 0.15924 | 0.095726 | 0 | 0 | 13.3 | 723.5367 | 717.06 | 712.8077 | 708.5667 | 704.3422 | 700.14 | 695.9663 | 691.8288 | 688.5311 | 686.3365 | 685.086 | 684.4919 | 684.2969 | 684.3177 | 684.4386 | 684.5938 | 684.7499 | 684.8884 | 684.9984 | 685.073 | 681.7783
13.4 | 0.79891 | 0.81763 | 0.81409 | 0.80876 | 0.80164 | 0.79271 | 0.78195 | 0.76173 | 0.72963 | 0.68729 | 0.63763 | 0.58322 | 0.52589 | 0.46676 | 0.40644 | 0.34525 | 0.28337 | 0.22097 | 0.15817 | 0.095095 | 0 | 0 | 13.4 | 723.5367 | 717.3315 | 713.2626 | 709.2055 | 705.1663 | 701.15 | 697.1627 | 694.0054 | 691.9388 | 690.8013 | 690.3058 | 690.1985 | 690.3032 | 690.5115 | 690.759 | 691.0063 | 691.2305 | 691.4202 | 691.5674 | 691.6666 | 688.4023
13.5 | 0.83772 | 0.85551 | 0.85188 | 0.84641 | 0.83909 | 0.82991 | 0.81121 | 0.78057 | 0.73961 | 0.6912 | 0.63791 | 0.58157 | 0.52332 | 0.46384 | 0.40353 | 0.34256 | 0.28107 | 0.21912 | 0.15683 | 0.094297 | 0 | 0 | 13.5 | 723.5367 | 717.6104 | 713.7295 | 709.8617 | 706.0126 | 702.1881 | 699.188 | 697.271 | 696.2733 | 695.905 | 695.9103 | 696.1134 | 696.4095 | 696.7411 | 697.0762 | 697.3931 | 697.6745 | 697.9078 | 698.0872 | 698.2077 | 694.9782
13.6 | 0.87469 | 0.89153 | 0.88779 | 0.88216 | 0.87464 | 0.85756 | 0.82849 | 0.78906 | 0.74213 | 0.69022 | 0.63514 | 0.57801 | 0.51952 | 0.46009 | 0.39997 | 0.33935 | 0.27832 | 0.21693 | 0.15525 | 0.093357 | 0 | 0 | 13.6 | 723.5367 | 717.8969 | 714.2095 | 710.5359 | 706.8826 | 704.0494 | 702.2947 | 701.4534 | 701.234 | 701.3786 | 701.7086 | 702.1173 | 702.5475 | 702.9707 | 703.3721 | 703.7417 | 704.0682 | 704.3397 | 704.5469 | 704.6858 | 701.4952
13.7 | 0.90976 | 0.92562 | 0.92177 | 0.91598 | 0.9006 | 0.87319 | 0.83539 | 0.79004 | 0.73967 | 0.68606 | 0.63032 | 0.57309 | 0.51478 | 0.45565 | 0.39591 | 0.33572 | 0.27521 | 0.21445 | 0.15346 | 0.092292 | 0 | 0 | 13.7 | 723.5367 | 718.1919 | 714.7034 | 711.2298 | 708.5717 | 706.9875 | 706.3124 | 706.2544 | 706.5548 | 707.0334 | 707.5813 | 708.1386 | 708.6747 | 709.1751 | 709.6331 | 710.0446 | 710.4048 | 710.7055 | 710.9371 | 711.0921 | 707.9439
13.8 | 0.94289 | 0.95774 | 0.95377 | 0.94018 | 0.91451 | 0.87841 | 0.83473 | 0.78599 | 0.73398 | 0.67978 | 0.62402 | 0.56709 | 0.50923 | 0.45061 | 0.39141 | 0.33178 | 0.27186 | 0.21175 | 0.1515 | 0.091118 | 0 | 0 | 13.8 | 723.5367 | 718.4956 | 715.2122 | 712.7382 | 711.3331 | 710.8323 | 710.9439 | 711.4098 | 712.0494 | 712.753 | 713.459 | 714.1346 | 714.7624 | 715.3338 | 715.8446 | 716.2937 | 716.6798 | 717.0005 | 717.2495 | 717.4187 | 714.316
13.9 | 0.97402 | 0.98782 | 0.97611 | 0.95227 | 0.91796 | 0.87603 | 0.82901 | 0.77867 | 0.7261 | 0.67194 | 0.61656 | 0.56016 | 0.50293 | 0.44499 | 0.38649 | 0.32755 | 0.26832 | 0.20891 | 0.14941 | 0.089848 | 0 | 0 | 13.9 | 723.5367 | 718.8087 | 716.5301 | 715.314 | 714.9965 | 715.2862 | 715.9255 | 716.7343 | 717.6033 | 718.4704 | 719.3019 | 720.0788 | 720.7899 | 721.4286 | 721.9914 | 722.4773 | 722.8874 | 723.2222 | 723.481 | 723.6587 | 720.6044
14 | 1.0031 | 1.0082 | 0.98629 | 0.95387 | 0.91378 | 0.86856 | 0.81997 | 0.76912 | 0.71664 | 0.66289 | 0.60809 | 0.5524 | 0.49593 | 0.43881 | 0.38114 | 0.32303 | 0.2646 | 0.20598 | 0.14726 | 0.088529 | 0 | 0 | 14 | 723.5367 | 719.9249 | 718.9097 | 718.7861 | 719.2638 | 720.0855 | 721.072 | 722.1142 | 723.1506 | 724.1476 | 725.0858 | 725.9532 | 726.7412 | 727.4442 | 728.0584 | 728.5826 | 729.0177 | 729.3662 | 729.6303 | 729.81 | 726.8026